## List
Type | Manufacturer | Model | Size | Orientation(s) | Approved | Renewed | ≤0.25% Pb | Manual | Shutoffs | Y-Spare Parts Only | Bypass | Meters | Notes
AVB | Ames | A100 | 0.75 | VUH | 1991-11-01 | 2012-11-01 | N | 8 |  | N
AVB | Ames | A100 | 1 | VUH | 1991-11-01 | 2012-11-01 | N | 8 |  | N
AVB | Ames | A100 | 1.5 | VUH | 1991-09-27 | 2012-09-27 | N | 8 |  | N
AVB | Ames | A100 | 2 | VUH | 1991-08-21 | 2012-08-21 | N | 8 |  | N
AVB | Watts | 288AM3 | 1.25 | VUH | 1991-08-12 | 2012-08-12 | N | 8 |  | N
AVB | Watts | 288AM3 | 1.5 | VUH | 1991-09-27 | 2012-09-27 | N | 8 |  | N
AVB | Watts | 288AM3 | 2 | VUH | 1991-08-21 | 2012-08-21 | N | 8 |  | N
AVB | Watts | 288AM3 | 2.5 | VUH | 1991-09-10 | 2012-09-10 | N | 8 |  | N
AVB | Watts | 288AM3 | 3 | VUH | 1991-09-16 | 2012-09-16 | N | 8 |  | N
AVB | Watts | 288AM5 | 0.75 | VUH | 1991-11-01 | 2012-11-01 | N | 8 |  | N
AVB | Watts | 288AM5 | 1 | VUH | 1991-11-01 | 2012-11-01 | N | 8 |  | N
DC | Ames | 2000-DC | 10 | H | 1987-08-04 | 2014-08-02 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DC
DC | Ames | 2000-DCA | 4 | H | 1988-01-11 | 2015-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-DCA | 6 | H | 1988-01-11 | 2015-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-DCA | 8 | H | 1988-01-11 | 2015-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-G-DC | 10 | H | 1987-08-04 | 2014-08-04 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DC
DC | Ames | 2000-G-DCA | 4 | H | 1988-01-11 | 2015-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-G-DCA | 6 | H | 1988-01-11 | 2015-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-G-DCA | 8 | H | 1988-01-11 | 2015-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000B | 0.5 | H | 1983-12-06 | 2013-12-06 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Ames | 2000B | 0.5 | H | 1997-06-16 | 2012-06-16 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Ames | 2000B | 0.5 | VU | 1997-06-16 | 2012-06-16 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 0.75 | H | 1993-04-05 | 2014-04-05 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 0.75 | VU | 1996-08-27 | 2014-08-27 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1 | H | 1991-02-26 | 2015-02-26 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Ames | 2000B | 1 | H | 1998-05-18 | 2013-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Ames | 2000B | 1 | VU | 1998-05-18 | 2013-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.25 | H | 1996-10-01 | 2014-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.25 | VU | 1996-10-01 | 2014-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.5 | H | 1994-05-24 | 2015-05-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.5 | VU | 1996-03-11 | 2014-03-11 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 2 | H | 1992-06-30 | 2013-06-30 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 2 | VU | 1996-03-08 | 2014-03-08 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B-FP | 0.75 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000B-FP | 1 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000B-FP | 1.25 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000B-FP | 1.5 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000B-FP | 2 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000BM3 | 0.75 | H | 2000-03-27 | 2015-03-27 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000BM3 | 0.75 | VU | 2000-03-27 | 2015-03-27 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000BM3-FP | 0.75 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000CIV | 4 | H | 1982-01-15 | 2015-01-15 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000CIV | 4 | VU | 1996-03-11 | 2014-03-11 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000CIV | 6 | H | 1982-05-18 | 2015-05-18 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000CIV | 6 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000CIV | 8 | H | 1981-07-06 | 2014-07-06 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000CIV | 8 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000CIV | 10 | H | 1983-03-16 | 2013-03-16 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000CIV | 10 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
DC | Ames | 2000SE | 2.5 | H | 1996-09-10 | 2014-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,mm,oo,pp,tt,uu,ccc,ddd,ffff,gggg | N
DC | Ames | 2000SE | 6 | H | 1993-11-22 | 2014-11-22 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Ames | 2000SE | 8 | H | 1992-09-09 | 2013-09-09 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Ames | 2000SS | 0.75 | H | 1995-05-05 | 2013-05-05 | N | 8 | ii | Y
DC | Ames | 2000SS | 1 | H | 1995-05-05 | 2013-05-05 | N | 8 | ii | Y
DC | Ames | 2000SS | 1.25 | H | 1995-07-14 | 2013-07-14 | N | 8 | ii | Y
DC | Ames | 2000SS | 1.5 | H | 1995-10-13 | 2013-10-13 | N | 8 | ii | Y
DC | Ames | 2000SS | 2 | H | 1995-10-13 | 2013-10-13 | N | 8 | ii | Y
DC | Ames | 2000SS | 2.5 | H | 1991-07-11 | 2012-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 2.5 | H | 1991-07-11 | 2012-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 3 | H | 1991-07-11 | 2012-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 3 | H | 1991-07-11 | 2012-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 4 | H | 1991-07-11 | 2012-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 4 | H | 1991-07-11 | 2012-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 6 | H | 1992-09-09 | 2013-09-09 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 6 | H | 1992-09-09 | 2013-09-09 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 8 | H | 1996-09-16 | 2014-09-16 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 8 | H | 1996-09-16 | 2014-09-16 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 10 | H | 2001-02-16 | 2013-02-16 | N | 8 | pp, | N
DC | Ames | 2000SS | 10 | H | 2001-02-16 | 2013-02-16 | Y | 8 | (ll),mm,oo | N
DC | Ames | 2000SS | 12 | VU | 2011-02-22 | 2014-02-22 | N | 9 | pp, | N
DC | Ames | 2000SS | 12 | VU | 2011-02-22 | 2014-02-22 | Y | 9 | (ll),mm,oo | N
DC | Ames | 2000SS | 12 | H | 2009-07-22 | 2012-07-22 | N | 9 | pp, | N
DC | Ames | 2000SS | 12 | H | 2009-07-22 | 2012-07-22 | Y | 9 | (ll),mm,oo | N
DC | Ames | 2000SS-M | 4 | H | 1995-05-05 | 2013-05-05 | N | 8 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N
DC | Ames | 2000SS-M | 6 | H | 1995-05-05 | 2013-05-05 | N | 8 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N
DC | Ames | 200B | 0.5 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 0.5 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 0.5 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 0.75 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 0.75 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 0.75 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1.25 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1.25 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1.25 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1.5 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1.5 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 1.5 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 2 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 2 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B | 2 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B R10 | 0.5 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B R10 | 0.5 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B R10 | 0.5 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B R10 | 0.75 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B R10 | 0.75 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B R10 | 0.75 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B-A | 0.5 | VUVD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B-A | 1 | VUVD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B-A | 1.25 | VUVD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B-A | 1.5 | VUVD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B-A | 2 | VUVD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B-AR10 | 0.5 | VUVD | 2013-07-03 |  | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 200B-AR10 | 0.75 | VUVD | 2013-07-03 |  | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | Colt 200 | 2.5 | H | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 2.5 | H | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 2.5 | VU | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 2.5 | VU | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 3 | H | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 3 | H | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 3 | VU | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 3 | VU | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 4 | H | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 4 | H | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 4 | VU | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 4 | VU | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 6 | H | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 6 | H | 2006-04-21 | 2015-04-21 | Y | 9 | yyy,zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 6 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 6 | VU | 2006-04-21 | 2015-04-21 | Y | 9 | yyy,zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 8 | H | 2004-08-11 | 2013-08-11 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 8 | H | 2004-08-11 | 2013-08-11 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 8 | VU | 2006-02-10 | 2015-02-10 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 8 | VU | 2006-02-10 | 2015-02-10 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 10 | H | 2008-05-02 | 2014-05-02 | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Ames | Colt 200 | 10 | H | 2008-05-02 | 2014-05-02 | Y | 9 | yyy,zzz,dddd,eeee,ggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 10 | VU | 2008-05-02 | 2014-05-02 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Ames | Colt 200 | 10 | VU | 2014-12-05 |  | Y | 9 | yyy,zzz,dddd,eeee,ggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200a | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),fff,qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200a | 2.5 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200a | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200a | 3 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200a | 4 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200a | 4 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200a | 6 | H | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200a | 6 | VU | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200N | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 3 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 4 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 6 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 6 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 8 | VUVD | 2013-01-03 |  | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Ames | Colt 200N | 8 | VUVD | 2013-01-03 |  | Y | 9 | yyy, zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 10 | VUVD | 2009-09-01 | 2012-09-01 | N | 9 | (ppp),qqq | N
DC | Ames | Colt 200N | 10 | VUVD | 2009-09-01 | 2012-09-01 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200Na | 2.5 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200Na | 3 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200Na | 4 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | Colt 200Na | 6 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Ames | DC | 4 | H | 1985-06-14 | 2012-06-14 | N | 6 | oo,pp,ffff,gggg | Y
DC | Ames | DC | 6 | H | 1985-06-14 | 2012-06-14 | N | 6 | oo,pp,ffff,gggg | Y
DC | Ames | DC | 8 | H | 1987-08-04 | 2014-08-04 | N | 7 | oo,pp,ffff,gggg | Y
DC | Ames | DC | 10 | [9 empty] | model designation changed to 2000-DC
DC | Ames | DC | 10 | [9 empty] | model designation changed to 2000-G-DC
DC | Ames | DCA | 4 | [9 empty] | model designation changed to 2000-DCA
DC | Ames | DCA | 4 | [9 empty] | model designation changed to 2000-G-DCA
DC | Ames | DCA | 6 | [9 empty] | model designation changed to 2000-DCA
DC | Ames | DCA | 6 | [9 empty] | model designation changed to 2000-G-DCA
DC | Ames | DCA | 8 | [9 empty] | model designation changed to 2000-DCA
DC | Ames | DCA | 8 | [9 empty] | model designation changed to 2000-G-DCA
DC | Ames | LF2000B | 0.5 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF2000B | 0.5 | VU | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 1 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 1 | VU | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 2 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 2 | VU | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM2 | 1.25 | H | 2013-09-25 |  | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM2 | 1.25 | VU | 2013-09-25 |  | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM2 | 1.5 | H | 2013-09-25 |  | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM2 | 1.5 | VU | 2013-09-25 |  | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM3 | 0.75 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM3 | 0.75 | VU | 2013-09-25 |  | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 0.5 | H | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 0.5 | VD | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 0.5 | VU | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 0.75 | H | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 0.75 | VD | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 0.75 | VU | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 1 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1.25 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1.25 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1.25 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1.5 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1.5 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 1.5 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 2 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 2 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B | 2 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B R10 | 0.5 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B R10 | 0.5 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B R10 | 0.5 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B R10 | 0.75 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B R10 | 0.75 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B R10 | 0.75 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B-A | 1 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B-A | 1.25 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B-A | 1.5 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LF200B-A | 2 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | LFU200B | 1 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1.25 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1.25 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1.25 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1.5 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1.5 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 1.5 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 2 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 2 | VD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | LFU200B | 2 | VU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | Maxim 200 | 2.5 | H | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 2.5 | H | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 2.5 | VU | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 2.5 | VU | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 3 | H | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 3 | H | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 3 | VU | 2004-07-20 | 2013-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 3 | VU | 2004-07-20 | 2013-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 4 | H | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 4 | H | 2006-04-21 | 2015-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 4 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 4 | VU | 2006-04-21 | 2015-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 6 | H | 2004-08-11 | 2013-08-11 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 6 | H | 2004-08-11 | 2013-08-11 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 6 | VU | 2006-02-10 | 2015-02-10 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 6 | VU | 2006-02-10 | 2015-02-10 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 8 | H | 2008-05-02 | 2014-05-02 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 8 | H | 2008-05-02 | 2014-05-02 | Y | 9 | (yyy),zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200 | 8 | VU | 2008-05-02 | 2014-05-02 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 8 | VU | 2008-05-02 | 2014-05-02 | Y | 9 | (yyy),zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200 | 10 | H | 2008-10-20 | 2014-10-20 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Ames | Maxim 200 | 10 | H | 2008-10-20 | 2014-10-20 | Y | 9 | yyy,zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200 | 10 | VU | 2008-10-20 | 2014-10-20 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Ames | Maxim 200 | 10 | VU | 2008-10-20 | 2014-10-20 | Y | 9 | yyy,zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200a | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200a | 2.5 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200a | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200a | 3 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200a | 4 | H | 2003-07-03 | 2012-07-03 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200a | 4 | VU | 2003-07-03 | 2012-07-03 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200N | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 3 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 4 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 6 | VUVD | 2013-01-03 |  | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Ames | Maxim 200N | 6 | VUVD | 2013-01-03 |  | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 8 | VUVD | 2009-09-01 | 2012-09-01 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 8 | VUVD | 2009-09-01 | 2012-09-01 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200Na | 2.5 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200Na | 3 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | Maxim 200Na | 4 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | N
DC | Ames | U200B | 1 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1.25 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1.25 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1.25 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1.5 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1.5 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 1.5 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 2 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 2 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200B | 2 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200BR10 | 0.5 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200BR10 | 0.5 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200BR10 | 0.5 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200BR10 | 0.75 | H | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200BR10 | 0.75 | VD | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Ames | U200BR10 | 0.75 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Apollo/Conbraco | 1/2DC | 0.5 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 1/2DC | 0.5 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 10DC | 10 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 10DC | 10 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 2 1/2DC | 2.5 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 2 1/2DC | 2.5 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 2 1/2DC-7 | 2.5 | H | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 2 1/2DC-7 | 2.5 | VU | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 2 1/2DC8 | 2.5 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 2 1/2DC8 | 2.5 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 2 1/2DCU | 2.5 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 2 1/2DCU | 2.5 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 3DC | 3 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 3DC | 3 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 3DC7 | 3 | H | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 3DC7 | 3 | VU | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 3DC8 | 3 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 3DC8 | 3 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 3DCU | 3 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 3DCU | 3 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 40-100-02 | 3 | H | 1991-04-08 | 2015-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-100-03 | 3 | H | 1991-04-08 | 2015-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-100-05 | 3 | H | 1998-12-08 | 2013-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-103-02 | 0.5 | H | 1995-05-01 | 2013-05-01 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-02 | 0.75 | H | 1989-03-17 | 2013-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-99T | 0.75 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-104-A2 | 0.75 | H | 1993-06-21 | 2014-06-21 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-A2T | 0.75 | H | 1992-03-25 | 2013-03-25 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-T2 | 0.75 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-104-TC2 | 0.75 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-105-02 | 1 | H | 1989-03-17 | 2013-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-105-99T | 1 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-105-A2 | 1 | H | 1993-06-21 | 2014-06-21 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-105-A2T | 1 | H | 1992-03-25 | 2013-03-25 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-105-T2 | 1 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-105-TC2 | 1 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-106-02 | 1.25 | H | 1992-04-06 | 2013-04-06 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-106-99T | 1.25 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-106-A2 | 1.25 | H | 1993-06-21 | 2014-06-21 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-106-A2T | 1.25 | H | 1993-05-22 | 2014-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-106-T2 | 1.25 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-107-02 | 1.5 | H | 1989-03-17 | 2013-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-107-99T | 1.5 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-107-A2 | 1.5 | H | 1993-05-22 | 2014-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-107-A2T | 1.5 | H | 1993-05-22 | 2014-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-107-T2 | 1.5 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-108-02 | 2 | H | 1989-03-17 | 2013-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-108-99T | 2 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-108-A2 | 2 | H | 1993-05-22 | 2014-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-108-A2T | 2 | H | 1993-05-22 | 2014-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-108-T2 | 2 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-109-02 | 2.5 | H | 1991-04-08 | 2015-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-109-03 | 2.5 | H | 1991-04-08 | 2015-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-109-05 | 2.5 | H | 1998-12-08 | 2013-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-10A-02 | 4 | H | 1991-04-08 | 2015-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10A-03 | 4 | H | 1991-04-08 | 2015-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10A-05 | 4 | H | 1998-12-08 | 2013-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-10A-06 | 4 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 40-10C-02 | 6 | H | 1991-04-08 | 2015-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10C-03 | 6 | H | 1991-04-08 | 2015-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10C-05 | 6 | H | 1998-12-08 | 2013-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-10C-06 | 6 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 40-10E-02 | 8 | H | 1991-10-22 | 2012-10-22 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10E-03 | 8 | H | 1991-10-22 | 2012-10-22 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10E-06 | 8 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 40-10G-02 | 10 | H | 1993-04-13 | 2014-04-13 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10G-03 | 10 | H | 1993-04-13 | 2014-04-13 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10G-06 | 10 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 4D-100 | 2.5 | VU | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 2.5 | H | 2012-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 3 | H | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 3 | VU | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 4 | H | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 4 | VU | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100U | 2.5 | VUVD | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100U | 3 | VUVD | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100U | 4 | VUVD | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4DC | 4 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 4DC | 4 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 4DC7 | 4 | H | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 4DC7 | 4 | VU | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 4DC8 | 4 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 4DC8 | 4 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 4DCU | 4 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 4S103 | 0.5 | [9 empty] | model designation changed to W432100
DC | Apollo/Conbraco | 4S103 | 0.5 | [9 empty] | model designation changed to W432100
DC | Apollo/Conbraco | 4SG-100 | 2.5 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 2.5 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 3 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 3 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 4 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 4 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 6 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 6 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 8 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 8 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100U | 2.5 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 3 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 4 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 6 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 8 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 6DC | 6 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 6DC | 6 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 6DC7 | 6 | H | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 6DC7 | 6 | VU | 2001-10-23 | 2013-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N
DC | Apollo/Conbraco | 6DC8 | 6 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 6DC8 | 6 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 6DCU | 6 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N
DC | Apollo/Conbraco | 8DC | 8 | H | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N
DC | Apollo/Conbraco | 8DC | 8 | VU | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N
DC | Apollo/Conbraco | 8DC8 | 8 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | 8DC8 | 8 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N
DC | Apollo/Conbraco | DC40 | 0.75 | H | 1996-06-27 | 2014-06-27 | N | 8 | (dd) | N |  |  | formerly 40-104-99T, 40-104-T2, 40-104-TC2
DC | Apollo/Conbraco | DC40 | 1 | H | 1996-06-27 | 2014-06-27 | N | 8 | (dd) | N |  |  | formerly 40-105-99T, 40-105-T2, 40-105-TC2
DC | Apollo/Conbraco | DC40 | 1.25 | H | 1996-10-09 | 2014-10-09 | N | 8 | (dd) | N |  |  | formerly 40-106-99T, 40-106-T2
DC | Apollo/Conbraco | DC40 | 1.5 | H | 1996-10-09 | 2014-10-09 | N | 8 | (dd) | N |  |  | formerly 40-107-99T, 40-107-T2
DC | Apollo/Conbraco | DC40 | 2 | H | 1996-10-09 | 2014-10-09 | N | 8 | (dd) | N |  |  | formerly 40-108-99T, 40-108-T2
DC | Apollo/Conbraco | DC4A | 0.5 | H | 2011-04-27 | 2014-04-27 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 0.5 | VU | 2011-04-27 | 2014-04-27 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 0.75 | H | 2011-04-27 | 2014-04-27 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 0.75 | VU | 2011-04-06 | 2014-04-06 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 1 | H | 2011-09-27 | 2014-09-27 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1 | VU | 2011-04-06 | 2014-04-06 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.25 | H | 2012-02-07 | 2015-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.25 | VU | 2012-02-07 | 2015-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.5 | H | 2012-02-07 | 2015-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.5 | VU | 2012-02-07 | 2015-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 2 | H | 2012-02-07 | 2015-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 2 | VU | 2012-03-27 | 2015-03-27 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4S | 0.5 | H | 2000-09-18 | 2012-09-18 | N | 9 | (dd) | N |  |  | formerly 1/2DC
DC | Apollo/Conbraco | DC4S | 0.5 | VU | 2000-09-18 | 2012-09-18 | N | 9 | (dd) | N |  |  | formerly 1/2DC
DC | Apollo/Conbraco | DC4S | 10 | H | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N |  |  | formerly 10DC
DC | Apollo/Conbraco | DC4S | 10 | VU | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N |  |  | formerly 10DC
DC | Apollo/Conbraco | DC4SG | 2.5 | H | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 2.5 | VU | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 3 | H | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 3 | VU | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 4 | H | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 4 | VU | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 6 | H | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 6 | VU | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 8 | H | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 8 | VU | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SGN | 2.5 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 3 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 4 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 6 | VUVD | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 8 | VUVD | 2007-09-25 | 2013-09-25 | N | 9 | (yyy)ppp,qqq,ttt | N |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DCLF4A | 0.5 | H | 2011-04-27 | 2014-04-27 | Y | 10 | (jjjjj),ttttt, uuuuu | N
DC | Apollo/Conbraco | DCLF4A | 0.5 | VU | 2011-04-27 | 2014-04-27 | Y | 10 | (jjjjj),ttttt, uuuuu | N
DC | Apollo/Conbraco | DCLF4A | 0.75 | H | 2011-04-27 | 2014-04-27 | Y | 9 | (jjjjj),ttttt | N
DC | Apollo/Conbraco | DCLF4A | 0.75 | VU | 2011-04-06 | 2014-04-06 | Y | 9 | (jjjjj),ttttt | N
DC | Apollo/Conbraco | DCLF4A | 1 | H | 2011-09-27 | 2014-09-27 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1 | VU | 2011-04-06 | 2014-04-06 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.25 | H | 2012-02-07 | 2015-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.25 | VU | 2012-02-07 | 2015-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.5 | H | 2012-02-07 | 2015-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.5 | VU | 2012-02-07 | 2015-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 2 | H | 2012-02-07 | 2015-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 2 | VU | 2012-03-27 | 2015-03-27 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 2.5 | H | 2013-11-05 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 2.5 | VU | 2013-11-05 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 3 | H | 2013-11-05 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 3 | VU | 2013-11-05 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 4 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 4 | VU | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 6 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 6 | VU | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 8 | H | 2014-05-15 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4A | 8 | VU | 2014-05-15 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4AN | 2.5 | VUVD | 2014-06-10 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4AN | 3 | VUVD | 2014-04-08 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4AN | 4 | VUVD | 2013-11-22 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4AN | 6 | VUVD | 2014-04-15 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4AN | 8 | VUVD | 2014-02-20 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 2.5 | H | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 2.5 | VU | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 3 | H | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 3 | VU | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 4 | H | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 4 | VU | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 6 | H | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | DCLF4SG | 6 | VU | 2015-01-23 |  | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn | N
DC | Apollo/Conbraco | W432100 | 0.5 | H | 2007-10-18 | 2013-10-18 | N | 9 | (dd) | N |  |  | formerly 4S103
DC | Apollo/Conbraco | W432100 | 0.5 | VU | 2007-10-18 | 2013-10-18 | N | 9 | (dd) | N |  |  | formerly 4S103
DC | ARI | DC 500 | 0.5 | H | 2013-01-03 |  | N | 9 | (ooooo), ii, ooo | N
DC | ARI | DC 500 | 0.5 | H | 2014-02-18 |  | Y | 9 | (ooooo) | N
DC | ARI | DC 500 | 0.75 | H | 2007-03-02 | 2013-03-02 | N | 9 | (ii),ooo, ooooo | N
DC | ARI | DC 500 | 0.75 | H | 2014-02-18 |  | Y | 9 | (ooooo) | N
DC | ARI | DC 500 | 1 | H | 2007-03-02 | 2013-03-02 | N | 9 | (ii),ooo, ooooo | N
DC | ARI | DC 500 | 1 | H | 2014-02-18 |  | Y | 9 | (ooooo) | N
DC | ARI | DC 500 | 1.25 | H | 2014-01-08 |  | Y | 10 | (ooooo) | N
DC | ARI | DC 500 | 1.5 | H | 2014-01-08 |  | Y | 10 | (ooooo) | N
DC | ARI | DC 500 | 2 | H | 2014-01-08 |  | Y | 10 | (ooooo) | N
DC | Cash Acme | DC 500 | 0.75 | H | 2012-04-19 | 2015-04-19 | Y | 9 | (ii),ooo | N
DC | Cash Acme | DC 500 | 1 | H | 2012-04-19 | 2015-04-19 | Y | 9 | (ii),ooo | N
DC | Cash Acme | DC100 | 0.75 | H | 2008-10-20 | 2014-10-20 | N | 8 | (ii) | N
DC | Cash Acme | DC100 | 1 | H | 2008-10-20 | 2014-10-20 | N | 8 | (ii) | N
DC | Cash Acme | DC100 | 1.5 | H | 2008-10-20 | 2014-10-20 | N | 8 | (ii) | N
DC | Cash Acme | DC100 | 2 | H | 2008-10-20 | 2014-10-20 | N | 8 | (ii) | N
DC | Cla-Val | D4 | 8 | H | 1989-06-22 | 2013-06-22 | N | 8 | (gg),hh,qq,rr | Y
DC | Cla-Val | D4 | 10 | H | 1989-06-22 | 2013-06-22 | N | 8 | (gg),hh,qq,rr | Y
DC | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
DC | Febco | 750 | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Febco | 750 | 10 | H | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Febco | 750 | 10 | VU | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 850 | 0.5 | VD | 2000-04-13 | 2015-04-13 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 0.5 | VU | 1999-12-17 | 2014-12-17 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 0.5 | H | 1997-11-21 | 2012-11-21 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 0.75 | VD | 2000-04-10 | 2015-04-10 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 0.75 | VU | 1999-12-17 | 2014-12-17 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 0.75 | H | 1997-11-21 | 2012-11-21 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1 | VD | 2000-01-14 | 2015-01-14 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1 | VU | 2000-09-07 | 2012-09-07 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1 | H | 1997-11-21 | 2012-11-21 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.25 | VD | 2000-04-13 | 2015-04-13 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.25 | VU | 1999-07-17 | 2014-07-17 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.25 | H | 1997-11-21 | 2012-11-21 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.5 | H | 1998-02-19 | 2013-02-19 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.5 | VD | 2000-04-13 | 2015-04-13 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.5 | VU | 1999-07-17 | 2014-07-17 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 2 | H | 1998-02-19 | 2013-02-19 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 2 | VD | 2000-04-10 | 2015-04-10 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 2 | VU | 1999-07-17 | 2014-07-17 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 2.5 | H | 1997-03-14 | 2015-03-14 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 2.5 | VU | 1997-03-19 | 2015-03-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 3 | H | 1997-03-14 | 2015-03-14 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 3 | VU | 1997-03-19 | 2015-03-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 4 | H | 1994-05-04 | 2015-05-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 4 | VU | 1995-02-07 | 2013-02-07 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 6 | H | 1994-05-04 | 2015-05-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 6 | VU | 1995-05-31 | 2013-05-31 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 8 | H | 1995-10-04 | 2013-10-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
DC | Febco | 850 | 8 | VU | 1996-10-14 | 2014-10-14 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
DC | Febco | 857 | 2.5 | H | 2006-08-01 | 2012-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | N
DC | Febco | 857 | 2.5 | VU | 2006-08-01 | 2012-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | N
DC | Febco | 857 | 3 | H | 2006-08-01 | 2012-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | N
DC | Febco | 857 | 3 | VU | 2006-08-01 | 2012-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | N
DC | Febco | 870 | 2.5 | VUVD | 1995-03-10 | 2013-03-10 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 3 | VUVD | 1995-03-10 | 2013-03-10 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 4 | VUVD | 1994-05-04 | 2015-05-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 6 | VUVD | 1994-05-04 | 2015-05-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 8 | VUVD | 1994-05-24 | 2015-05-24 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 10 | VUVD | 1996-10-04 | 2014-10-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 750 | 2.5 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750 | 2.5 | H | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 2.5 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750 | 2.5 | VU | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 3 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750 | 3 | H | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 3 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750 | 3 | VU | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 4 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750 | 4 | H | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 4 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750 | 4 | VU | 2009-09-17 | 2012-09-17 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 6 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Febco | 750 | 6 | H | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 6 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Febco | 750 | 6 | VU | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 8 | H | 2009-09-17 | 2012-09-17 | N | 9 | (yyy),ppp,qqq,aaaa,bbbb | N
DC | Febco | 750 | 8 | H | 2009-09-17 | 2012-09-17 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750 | 8 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (yyy),ppp,qqq,aaaa,bbbb | N
DC | Febco | 750 | 8 | VU | 2009-09-17 | 2012-09-17 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750N | 2.5 | VUVD | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750N | 2.5 | VUVD | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750N | 3 | VUVD | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750N | 3 | VUVD | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750N | 4 | VUVD | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750N | 4 | VUVD | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 750N | 6 | VUVD | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq | N
DC | Febco | 750N | 6 | VUVD | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Febco | 805 Type YD | 2.5 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 3 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 4 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 6 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 8 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 10 | [9 empty] | model designation changed to 805YD
DC | Febco | 805Y | 0.75 | H | 1982-05-13 | 2015-05-13 | N | 6 | ii,fff,jjj,ooo | Y
DC | Febco | 805Y | 1 | H | 1982-05-13 | 2015-05-13 | N | 6 | ii,fff,jjj,ooo | Y
DC | Febco | 805Y | 1.5 | H | 1983-01-05 | 2013-01-05 | N | 6 | ii,fff,jjj,ooo | Y
DC | Febco | 805Y | 2 | H | 1983-01-05 | 2013-01-05 | N | 6 | ii,fff,ooo | Y
DC | Febco | 805YB | 0.75 | H | 1994-05-04 | 2015-05-04 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable seats beginning with Serial No. A105801
DC | Febco | 805YB | 0.75 | VU | 1996-04-16 | 2014-04-16 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable seats beginning with Serial No. A105801
DC | Febco | 805YD | 2.5 | H | 1987-05-31 | 2014-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N |  |  | formerly 805 Type YD
DC | Febco | 805YD | 3 | H | 1987-05-31 | 2014-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N |  |  | formerly 805 Type YD
DC | Febco | 805YD | 4 | H | 1987-05-31 | 2014-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N |  |  | formerly 805 Type YD
DC | Febco | 805YD | 6 | H | 1987-05-31 | 2014-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N |  |  | formerly 805 Type YD
DC | Febco | 805YD | 8 | H | 1987-05-31 | 2014-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N |  |  | formerly 805 Type YD
DC | Febco | 805YD | 10 | H | 1987-05-31 | 2014-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N |  |  | formerly 805 Type YD
DC | Febco | 805YR | 0.75 | H | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj,ooo | Y
DC | Febco | 805YR | 1 | H | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj,ooo | Y
DC | Febco | 850F | 0.75 | H | 2001-09-28 | 2013-09-28 | N | 9 | fff,jjj | Y
DC | Febco | 850F | 0.75 | VD | 2001-09-28 | 2013-09-28 | N | 9 | (fff),jjj | N
DC | Febco | 850F | 0.75 | VU | 2001-09-28 | 2013-09-28 | N | 9 | (fff),jjj | N
DC | Febco | 850U | 0.5 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.5 | VU | 1999-12-17 | 2014-12-17 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.5 | VD | 2000-10-16 | 2012-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.75 | H | 1999-03-08 | 2014-03-08 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.75 | VU | 1999-12-17 | 2014-12-17 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.75 | VD | 2000-10-16 | 2012-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 1 | H | 1999-08-04 | 2014-08-04 | N | 9 | (kkk) | N
DC | Febco | 850U | 1 | VD | 2000-01-14 | 2015-01-14 | N | 9 | (kkk) | N
DC | Febco | 850U | 1 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.25 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.25 | VU | 1999-08-04 | 2014-08-04 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.25 | VD | 2000-10-16 | 2012-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.5 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.5 | VU | 1999-08-04 | 2014-08-04 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.5 | VD | 2000-10-16 | 2012-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 2 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 2 | VU | 1999-08-04 | 2014-08-04 | N | 9 | (kkk) | N
DC | Febco | 850U | 2 | VD | 2000-10-16 | 2012-10-16 | N | 9 | (kkk) | N
DC | Febco | 870V | 2.5 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 2.5 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 3 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 3 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 4 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 4 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 6 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 6 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 8 | VUVD | 1997-01-06 | 2014-01-06 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 8 | VUVU | 1997-01-06 | 2014-01-06 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 10 | VUVD | 1997-07-11 | 2012-07-11 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | 870V | 10 | VUVU | 1997-07-11 | 2012-07-11 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | N
DC | Febco | LF850 | 0.5 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 0.75 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.25 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.5 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 2 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 2.5 | H | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 2.5 | VU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 3 | H | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 3 | VU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 4 | H | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 4 | VU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 6 | H | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 6 | VU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 8 | H | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 8 | VU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 10 | H | 2013-06-24 |  | Y | 9 | (mm),ll | N
DC | Febco | LF850 | 10 | VU | 2013-06-24 |  | Y | 9 | (mm),ll | N
DC | Febco | LF850U | 0.5 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 0.75 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.25 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.5 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 2 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF870V | 2.5 | VUVD | 2012-08-09 |  | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 2.5 | VUVU | 2012-08-09 |  | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 3 | VUVD | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 3 | VUVU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 4 | VUVD | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 4 | VUVU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 6 | VUVD | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 6 | VUVU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 8 | VUVD | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Febco | LF870V | 8 | VUVU | 2012-05-22 | 2015-05-22 | Y | 9 | (mm),ll | N
DC | Flomatic | DCV | 0.75 | H | 1994-05-04 | 2015-05-04 | N | 8 | ii | Y
DC | Flomatic | DCV | 1 | H | 1994-05-04 | 2015-05-04 | N | 8 | ii | Y
DC | Flomatic | DCV | 1.5 | H | 1995-05-10 | 2013-05-10 | N | 8 | ii | Y
DC | Flomatic | DCV | 2 | H | 1995-05-10 | 2013-05-10 | N | 8 | ii | Y
DC | Flomatic | DCV | 2.5 | H | 1997-02-14 | 2015-02-14 | N | 8 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd | Y
DC | Flomatic | DCV | 3 | H | 1997-02-14 | 2015-02-14 | N | 8 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd | Y
DC | Flomatic | DCV | 4 | H | 1999-07-01 | 2014-07-01 | N | 9 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd,ddddd | Y
DC | Flomatic | DCV | 4 | H | 1999-07-01 | 2014-07-01 | Y | 9 | ddddd | Y
DC | Flomatic | DCV | 6 | H | 2002-01-31 | 2014-01-31 | N | 9 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd,ddddd | Y
DC | Flomatic | DCV | 6 | H | 2002-01-31 | 2014-01-31 | Y | 9 | ddddd | Y
DC | Flomatic | DCV | 8 | H | 2004-11-09 | 2013-11-09 | N | 9 | (mm), hh, jj, kk, ll, gg, yy, zz, ccc, ddd | Y
DC | Flomatic | DCVE | 0.75 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
DC | Flomatic | DCVE | 1 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
DC | Flomatic | DCVE | 1.5 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
DC | Flomatic | DCVE | 2 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
DC | Hersey | 2 | 3 | H | 1978-12-27 | 2014-12-27 | N | 5 | tt,bb,qq,iii,lll | Y
DC | Hersey | 2 | 4 | H | 1978-12-27 | 2014-12-27 | N | 5 | tt,bb,qq,iii,lll | Y
DC | Hersey | 2 | 6 | H | 1978-12-22 | 2014-12-22 | N | 5 | tt,bb,qq,iii,lll | Y
DC | Hersey | 2 | 8 | H | 1981-07-06 | 2014-07-06 | N | 6 | tt,bb,qq,iii,lll | Y
DC | Hersey | 2 | 10 | H | 1982-02-19 | 2015-02-19 | N | 6 | tt,bb,qq,iii,lll | Y
DC | Neptune | [5 empty] | N | [5 empty] | See Wilkins
DC | Watts | 7 | 2.5 | VU | 1996-08-27 | 2014-08-27 | Y | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | N
DC | Watts | 7 | 3 | VU | 1996-08-27 | 2014-08-27 | Y | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,eee,ffff,gggg | N
DC | Watts | 709 | 4 | VU | 1996-03-11 | 2014-03-11 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709 | 6 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709 | 8 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709 | 10 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 757 | 2.5 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 2.5 | H | 2004-09-29 | 2013-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 2.5 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 2.5 | VU | 2004-09-29 | 2013-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 3 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 3 | H | 2004-09-29 | 2013-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 3 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 3 | VU | 2004-09-29 | 2013-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 4 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 4 | H | 2004-09-29 | 2013-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 4 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 4 | VU | 2004-09-29 | 2013-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 6 | H | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 6 | H | 2006-04-21 | 2015-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 6 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 6 | VU | 2006-04-21 | 2015-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 8 | H | 2004-09-16 | 2013-09-16 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 8 | H | 2004-09-16 | 2013-09-16 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 8 | VU | 2006-02-10 | 2015-02-10 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 8 | VU | 2006-02-10 | 2015-02-10 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 10 | H | 2008-05-02 | 2014-05-02 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 10 | H | 2008-05-02 | 2014-05-02 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 10 | VU | 2008-05-02 | 2014-05-02 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 10 | VU | 2008-05-02 | 2014-05-02 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 2.5 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 2.5 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 3 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 3 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 4 | H | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 4 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 6 | H | 2004-09-16 | 2013-09-16 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 6 | VU | 2006-02-10 | 2015-02-10 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 8 | H | 2008-05-02 | 2014-05-02 | N | 9 | (yyy), ppp, qqq,zzz, aaaa, bbbb, dddd, eeee, ffff, gggg,nnnnn | N
DC | Watts | 767 | 8 | VU | 2008-05-02 | 2014-05-02 | N | 9 | (yyy), ppp, qqq,zzz, aaaa, bbbb, dddd, eeee, ffff, gggg,nnnnn | N
DC | Watts | 767 | 10 | H | 2008-10-20 | 2014-10-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg | N
DC | Watts | 767 | 10 | VU | 2008-10-20 | 2014-10-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg | N
DC | Watts | 774 | 8 | H | 1996-09-16 | 2014-09-16 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 8 | H | 1996-09-16 | 2014-09-16 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 10 | H | 2001-02-16 | 2013-02-16 | Y | 8 | (ll),mm,ffff,gggg | N
DC | Watts | 774 | 12 | H | 2010-01-12 | 2013-01-12 | N | 9 | hh,gg | N
DC | Watts | 774 | 12 | H | 2010-01-12 | 2013-01-12 | N | 9 | (ll),mm | N
DC | Watts | 007 | 2.5 | H | 1990-09-30 | 2014-09-30 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | N
DC | Watts | 007 | 3 | H | 1990-09-30 | 2014-09-30 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,eee,ffff,gggg | N
DC | Watts | 007M1-FP | 1 | H | 2009-09-01 | 2012-09-01 | Y | 9 | (eeeee) | N
DC | Watts | 007M1-FP | 2 | H | 2009-09-01 | 2012-09-01 | Y | 9 | (eeeee) | N
DC | Watts | 007M1PCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | Y | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1PCQT | 1 | H | 1993-12-10 | 2014-12-10 | Y | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | Y | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007M1PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1QT | 0.75 | H | 1991-02-26 | 2015-02-26 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007M1QT | 1 | H | 1991-02-26 | 2015-02-26 | N | 8 | (vv),xx,ooo,hhhh,pppp | N |  |  | Upgraded to 9th Ed.
DC | Watts | 007M1QT | 1 | H | 1998-05-18 | 2013-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | Previous 8th Ed. Approval
DC | Watts | 007M1QT | 1 | VU | 1998-05-18 | 2013-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1QT | 1.5 | H | 1992-06-30 | 2013-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007M1QT | 2 | H | 1992-06-30 | 2013-06-30 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1QT | 2 | VU | 1996-03-08 | 2014-03-08 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2-FP | 1.25 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Watts | 007M2-FP | 1.5 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Watts | 007M2PCQT | 1.25 | H | 1996-12-09 | 2014-12-09 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2PCQT | 1.25 | VU | 1996-12-09 | 2014-12-09 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2PCQT | 1.5 | H | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 0.75 | H | 1993-04-05 | 2014-04-05 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 0.75 | VU | 1996-08-27 | 2014-08-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.25 | H | 1996-10-01 | 2014-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.25 | VU | 1996-10-01 | 2014-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.5 | H | 1994-05-24 | 2015-05-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.5 | VU | 1996-03-11 | 2014-03-11 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M3-FP | 0.75 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
DC | Watts | 007M3QT | 0.75 | H | 1999-10-18 | 2014-10-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M3QT | 0.75 | VU | 1999-10-18 | 2014-10-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007PCQT | 0.5 | H | 1995-02-17 | 2013-02-17 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007QT | 0.5 | H | 1997-06-16 | 2012-06-16 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Watts | 007QT | 0.5 | VU | 1997-06-16 | 2012-06-16 | N | 9 | (vv),xx,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Watts | 007QT | 0.5 | H | 1993-12-06 | 2014-12-08 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Watts | 007QT | 0.5 | VU | 1996-04-19 | 2014-04-19 | N | 8 | pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Watts | 007QT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | pppp,rrrrr | Y
DC | Watts | 007QT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | pppp,rrrrr | Y
DC | Watts | 007QT | 1.5 | H | 1988-07-21 | 2012-07-21 | N | 7 | pppp,rrrrr | Y |  |  | Upgraded to 9th Ed.
DC | Watts | 007QT | 2 | H | 1988-07-21 | 2012-07-21 | N | 7 | pppp,rrrrr | Y |  |  | Upgraded to 9th Ed.
DC | Watts | 007SSM1PCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSM1PCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSM1QT | 0.75 | H | 1991-02-26 | 2015-02-26 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSM1QT | 1 | H | 1991-02-26 | 2015-02-26 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSPCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSPCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSQT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | pppp | Y
DC | Watts | 007SSQT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | pppp | Y
DC | Watts | 007SSQT | 1.5 | H | 1988-07-21 | 2012-07-21 | N | 7 | pppp | Y
DC | Watts | 007SSQT | 2 | H | 1988-07-21 | 2012-07-21 | N | 7 | pppp | Y
DC | Watts | 700 | 2.5 | H | 1981-01-10 | 2014-01-10 | N | 5 |  | Y
DC | Watts | 700 | 3 | H | 1981-01-10 | 2014-01-10 | N | 5 |  | Y
DC | Watts | 709 | 2.5 | H | 1986-06-12 | 2013-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,ffff,gggg | N
DC | Watts | 709 | 3 | H | 1986-06-12 | 2013-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709 | 4 | H | 1982-01-15 | 2015-01-15 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709 | 6 | H | 1982-05-18 | 2015-05-18 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709 | 8 | H | 1981-07-06 | 2014-07-06 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709 | 10 | H | 1983-03-16 | 2013-03-16 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N
DC | Watts | 709BB | 2.5 | H | 1982-07-20 | 2012-07-20 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | N
DC | Watts | 709BB | 3 | H | 1982-07-20 | 2012-07-20 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | N
DC | Watts | 709QT | 0.75 | H | 1982-08-04 | 2012-08-04 | N | 6 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 709QT | 1 | H | 1982-08-04 | 2012-08-04 | N | 6 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 709QT | 1.5 | H | 1982-04-27 | 2015-04-21 | N | 6 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 709QT | 2 | H | 1982-04-27 | 2015-04-21 | N | 6 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 719AQT | 0.5 | VUVD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 1 | VUVD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 1.25 | VUVD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 1.5 | VUVD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 2 | VUVD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQTR10 | 0.5 | VUVD | 2013-07-03 |  | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 719AQTR10 | 0.75 | VUVD | 2013-07-03 |  | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 719QT | 0.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.5 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.75 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.75 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.75 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.25 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.25 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.25 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.5 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 2 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 2 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 2 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QTR10 | 0.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | N
DC | Watts | 719QTR10 | 0.5 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | N
DC | Watts | 719QTR10 | 0.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | N
DC | Watts | 719QTR10 | 0.75 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | N
DC | Watts | 719QTR10 | 0.75 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | N
DC | Watts | 719QTR10 | 0.75 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | N
DC | Watts | 757a | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757a | 2.5 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757a | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757a | 3 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757a | 4 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757a | 4 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757a | 6 | H | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757a | 6 | VU | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757N | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 3 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 4 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 6 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 6 | VUVD | 2009-04-07 | 2015-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 8 | VUVD | 2013-01-03 |  | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Watts | 757N | 8 | VUVD | 2013-01-03 |  | Y | 9 | yyy, zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 10 | VUVD | 2009-09-01 | 2012-09-01 | N | 9 | (ppp),qqq | N
DC | Watts | 757N | 10 | VUVD | 2009-09-01 | 2012-09-01 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757Na | 2.5 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757Na | 3 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757Na | 4 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757Na | 6 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757NQT | 2.5 | VUVD | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757NQT | 3 | VUVD | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757NQT | 4 | VUVD | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 2.5 | H | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 2.5 | VU | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 3 | H | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 3 | VU | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 4 | H | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 4 | VU | 2009-12-04 | 2012-12-04 | Y | 9 | fffff | N
DC | Watts | 767a | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767a | 2.5 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767a | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767a | 3 | VU | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767a | 4 | H | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767a | 4 | VU | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767N | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767N | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767N | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767N | 6 | VUVD | 2013-01-03 |  | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Watts | 767N | 6 | VUVD | 2013-01-03 |  | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 767N | 8 | VUVD | 2009-09-01 | 2012-09-01 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767Na | 2.5 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767Na | 3 | VUVD | 2003-03-20 | 2015-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767Na | 4 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 770 | 4 | H | 1992-05-20 | 2013-05-20 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu,yy | Y
DC | Watts | 770 | 8 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu,yy | Y
DC | Watts | 770QTFDA | 4 | H | 1993-01-12 | 2014-01-13 | N | 8 | ww | Y
DC | Watts | 770QTFDA | 8 | H | 1993-01-12 | 2014-01-13 | N | 8 | ww | Y
DC | Watts | 772 | 4 | H | 1992-07-01 | 2013-07-01 | N | 8 | oo,yy | Y
DC | Watts | 772 | 10 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo,yy | Y
DC | Watts | 774 | 2.5 | H | 1991-07-11 | 2012-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 2.5 | H | 1991-07-11 | 2012-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 3 | H | 1991-07-11 | 2012-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 3 | H | 1991-07-11 | 2012-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 4 | H | 1991-07-11 | 2012-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 4 | H | 1991-07-11 | 2012-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 6 | H | 1992-09-09 | 2013-09-09 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 6 | H | 1992-09-09 | 2013-09-09 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 12 | VU | 2011-03-21 | 2014-03-21 | N | 9 | pp, | N
DC | Watts | 774 | 12 | VU | 2011-03-21 | 2014-03-21 | Y | 9 | (ll),mm,oo | N
DC | Watts | 774X | 2.5 | H | 1996-09-10 | 2014-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | N
DC | Watts | 774X | 6 | H | 1993-11-22 | 2014-11-22 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Watts | 774X | 8 | H | 1992-09-09 | 2013-09-09 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Watts | 775QT | 0.5 | H | 2000-02-01 | 2015-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 0.5 | VU | 2000-02-01 | 2015-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 0.75 | H | 2000-02-01 | 2015-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 0.75 | VU | 2000-02-01 | 2015-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 1 | H | 1999-08-12 | 2014-08-12 | N | 9 | int | Y
DC | Watts | 775QT | 1 | VU | 1999-08-12 | 2014-08-12 | N | 9 | int | Y
DC | Watts | 775QT | 1.25 | H | 2000-09-07 | 2012-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 1.25 | VU | 2000-09-07 | 2012-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 1.5 | H | 2000-09-07 | 2012-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 1.5 | VU | 2000-09-07 | 2012-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 2 | H | 2002-03-28 | 2014-03-28 | N | 9 | int | Y
DC | Watts | 775QT | 2 | VU | 2002-03-28 | 2014-03-28 | N | 9 | int | Y
DC | Watts | LF007 | 2.5 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (oo) | N
DC | Watts | LF007 | 3 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (oo) | N
DC | Watts | LF007M1PCQT | 1 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1PCQT | 1 | VU | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1PCQT | 2 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1PCQT | 2 | VU | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 1 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 1 | VU | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 2 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 2 | VU | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.25 | H | 2008-01-11 | 2014-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.25 | VU | 2008-01-11 | 2014-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.5 | H | 2008-01-11 | 2014-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.5 | VU | 2008-01-11 | 2014-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M3PCQT | 0.75 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3PCQT | 0.75 | VU | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3QT | 0.75 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3QT | 0.75 | VU | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007PCQT | 0.5 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007PCQT | 0.5 | VU | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007QT | 0.5 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007QT | 0.5 | VU | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF709 | 2.5 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 3 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (ll) oo | N
DC | Watts | LF709 | 4 | H | 2012-07-27 |  | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 4 | VU | 2012-07-27 |  | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 6 | H | 2012-07-27 |  | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 6 | VU | 2012-07-27 |  | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 8 | H | 2010-07-01 | 2013-07-01 | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 8 | VU | 2010-07-01 | 2013-07-01 | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 10 | H | 2010-07-01 | 2013-07-01 | Y | 9 | (ll), oo | N
DC | Watts | LF709 | 10 | VU | 2010-07-01 | 2013-07-01 | Y | 9 | (ll), oo | N
DC | Watts | LF719AQT | 1 | VUVD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 1 | VUVD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719AQT | 1.25 | VUVD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 1.25 | VUVD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719AQT | 1.5 | VUVD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 1.5 | VUVD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719AQT | 2 | VUVD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 2 | VUVD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 0.5 | H | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.5 | VD | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.5 | VU | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.75 | H | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.75 | VD | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.75 | VU | 2013-07-03 |  | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 1 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.25 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.25 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.25 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.25 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.25 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.25 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.5 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.5 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.5 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.5 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.5 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.5 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 2 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 2 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 2 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 2 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 2 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 2 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QTR10 | 0.5 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | LF719QTR10 | 0.5 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | LF719QTR10 | 0.5 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | LF719QTR10 | 0.75 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | LF719QTR10 | 0.75 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | LF719QTR10 | 0.75 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | LFU719QT | 1 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.25 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.25 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.25 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.25 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.25 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.25 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.5 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.5 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.5 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.5 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.5 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.5 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 2 | H | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 2 | H | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 2 | VD | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 2 | VD | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 2 | VU | 2005-08-22 | 2014-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 2 | VU | 2005-08-22 | 2014-08-22 | Y | 9 | hhhh | N
DC | Watts | SS007M1QT | 1 | H | 1998-05-18 | 2013-05-18 | Y | 9 | (hhh) | N
DC | Watts | SS007M1QT | 1 | VU | 1998-05-18 | 2013-05-18 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.5 | H | 2000-09-11 | 2012-09-11 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.5 | VU | 2000-09-11 | 2012-09-11 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.75 | H | 2000-09-07 | 2012-09-07 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.75 | VU | 2000-09-07 | 2012-09-07 | Y | 9 | (hhh) | N
DC | Watts | U007M1APCQT | 0.75 | VDVD | 1994-12-10 | 2012-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 0.75 | VDVU | 1994-12-10 | 2012-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 0.75 | VUVD | 1994-12-10 | 2012-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 0.75 | VUVU | 1994-12-10 | 2012-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VDVD | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VDVU | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VUVD | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VUVU | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VDVD | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VDVU | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VUVD | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VUVU | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VDVD | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VDVU | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VUVD | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VUVU | 1994-02-24 | 2015-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1QT | 0.75 | H | 1993-08-30 | 2014-08-28 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1QT | 1 | H | 1993-08-30 | 2014-08-30 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1QT | 1.5 | H | 1993-10-20 | 2014-10-20 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007M1QT | 2 | H | 1993-10-20 | 2014-10-20 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VDVD | 1994-09-06 | 2012-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VDVU | 1994-09-06 | 2012-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VUVD | 1994-09-06 | 2012-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VUVU | 1994-09-06 | 2012-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2QT | 1.25 | H | 1996-10-01 | 2014-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2QT | 1.5 | H | 1994-09-06 | 2012-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007PCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007PCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 0.5 | H | 1999-03-08 | 2014-03-08 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007QT | 0.5 | VU | 1999-03-08 | 2014-03-08 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007QT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 1.5 | H | 1988-07-21 | 2012-07-21 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 2 | H | 1988-07-21 | 2012-07-21 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007SSPCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSPCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSPCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSPCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 1.5 | H | 1988-07-21 | 2012-07-21 | N | 7 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 2 | H | 1988-07-21 | 2012-07-21 | N | 7 | vv,xx,pppp | Y
DC | Watts | U719QT | 0.5 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.5 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.5 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.75 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.75 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.75 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 1 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.25 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.25 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.25 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.5 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 2 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 2 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 2 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QTR10 | 0.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.5 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.75 | H | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.75 | VD | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.75 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | formerly U719QT
DC | Wilkins | 350 | 0.75 | H | 2005-07-06 | 2014-07-06 | N | 9 | (ii),ooo | N
DC | Wilkins | 350 | 0.75 | VU | 2005-07-06 | 2014-07-06 | N | 9 | (ii),ooo | N
DC | Wilkins | 350 | 1 | H | 2006-04-21 | 2015-04-21 | N | 9 | (ii),ooo | N
DC | Wilkins | 350 | 1 | VU | 2006-04-21 | 2015-04-21 | N | 9 | (ii),ooo | N
DC | Wilkins | 350 | 1.25 | H | 2009-01-08 | 2015-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 1.25 | VU | 2009-01-08 | 2015-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 1.5 | H | 2009-01-08 | 2015-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 1.5 | VU | 2009-01-08 | 2015-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 2 | H | 2009-01-08 | 2015-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 2 | VU | 2009-01-08 | 2015-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 2.5 | H | 2001-09-05 | 2013-09-05 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 2.5 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 2.5 | VU | 2002-04-03 | 2014-04-03 | N | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 2.5 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 3 | H | 2001-09-05 | 2013-09-05 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 3 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 3 | VU | 2002-04-03 | 2014-04-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 3 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 4 | H | 1999-09-15 | 2014-09-15 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 4 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 4 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 4 | VU | 2000-09-07 | 2012-09-07 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 6 | H | 1999-10-18 | 2014-10-18 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 6 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 6 | VU | 1999-12-17 | 2014-12-17 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 6 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 8 | H | 2002-03-08 | 2014-03-08 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 8 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 8 | VU | 2003-01-16 | 2015-01-16 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 8 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 10 | H | 2002-08-28 | 2014-08-28 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 10 | VU | 2003-03-14 | 2015-03-14 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 10 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 12 | H | 2009-02-10 | 2015-02-10 | N | 9 | (hh),ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 12 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (hh),ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 450 | 2.5 | VUVD | 2002-01-24 | 2014-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 2.5 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 3 | VUVD | 2002-01-24 | 2014-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 3 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 4 | VUVD | 2000-04-12 | 2015-04-12 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 4 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 6 | VUVD | 2000-05-24 | 2015-05-24 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 6 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 8 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 8 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 10 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 10 | VUVD | 2003-09-11 | 2012-09-11 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number K01185
DC | Wilkins | 950 | 4 | VU | 1995-08-29 | 2013-08-29 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 6 | VU | 1995-08-29 | 2013-08-29 | N | 8 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 8 | VU | 1995-08-29 | 2013-08-29 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 950 | 10 | H | 1994-04-12 | 2015-04-12 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350A | 2.5 | H | 2005-06-22 | 2014-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 2.5 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350A | 2.5 | VU | 2005-06-22 | 2014-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 2.5 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 3 | H | 2005-06-22 | 2014-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 3 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 3 | VU | 2005-06-22 | 2014-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 3 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 4 | H | 2004-03-16 | 2013-03-16 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 4 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 4 | VU | 2004-03-16 | 2013-03-16 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 4 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 6 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 6 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 6 | H | 2003-11-25 | 2012-11-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 6 | VU | 2003-11-25 | 2012-11-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 8 | H | 2004-02-12 | 2013-02-12 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 8 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 8 | VU | 2004-02-12 | 2013-02-12 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 8 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 10 | H | 2006-04-06 | 2015-04-06 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 10 | VU | 2006-04-06 | 2015-04-06 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 10 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350AR | 2.5 | H | 2010-06-16 | 2013-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" Up to serial number U26097
DC | Wilkins | 350AR | 2.5 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 2.5 | VU | 2010-06-16 | 2013-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 2.5 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 3 | H | 2010-06-16 | 2013-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350AR | 3 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350AR | 3 | VU | 2010-06-16 | 2013-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350AR | 3 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350AR | 4 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350AR | 4 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350AR | 4 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350AR | 4 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350AR | 6 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350AR | 6 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350AR | 6 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 6 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350AR | 8 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 8 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350AR | 8 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 8 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350AR | 10 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350AR | 10 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 10 | VU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350ARXL | 2.5 | H | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350ARXL | 2.5 | VU | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350ARXL | 3 | H | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350ARXL | 3 | VU | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350ARXL | 4 | H | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350ARXL | 4 | VU | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350ARXL | 6 | H | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350ARXL | 6 | VU | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350ARXL | 8 | H | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350ARXL | 8 | VU | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350ARXL | 10 | H | 2010-06-05 | 2013-06-05 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350ARXL | 10 | VU | 2010-06-05 | 2013-06-05 | Y | 9 | (hh),ssss,tttt,xxxx,yyyy,zzzz,aaaaa | N |  |  | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350AST | 2.5 | H | 2011-11-29 | 2014-10-29 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 2.5 | VU | 2012-11-09 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 3 | H | 2011-11-29 | 2014-10-29 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 3 | VU | 2012-11-09 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 4 | H | 2011-11-29 | 2014-10-29 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 4 | VU | 2012-11-09 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 6 | H | 2012-03-27 | 2015-03-27 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 6 | VU | 2012-10-24 |  | Y | 10 | (yyy), ssss, uuuu,vvvv, xxxx, yyyy, aaaaa,kkkkk, lllll | N
DC | Wilkins | 350AST | 8 | H | 2014-02-20 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 8 | VU | 2014-02-20 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 10 | H | 2014-02-20 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350AST | 10 | VU | 2014-02-20 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
DC | Wilkins | 350ASTR | 2.5 | H | 2012-06-12 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350ASTR | 2.5 | VU | 2012-06-12 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350ASTR | 3 | H | 2012-06-12 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350ASTR | 3 | VU | 2012-06-12 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350ASTR | 4 | H | 2012-06-12 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350ASTR | 4 | VU | 2012-06-12 |  | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350ASTR | 6 | H | 2012-06-12 |  | Y | 10 | (yyy), ssss, uuuu,vvvv, xxxx, yyyy, aaaaa,kkkkk, lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350ASTR | 6 | VU | 2012-06-12 |  | Y | 10 | (yyy), ssss, uuuu,vvvv, xxxx, yyyy, aaaaa,kkkkk, lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350ASTR | 8 | H | 2014-02-25 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DC | Wilkins | 350ASTR | 8 | VU | 2014-02-25 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DC | Wilkins | 350ASTR | 10 | H | 2014-02-25 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DC | Wilkins | 350ASTR | 10 | VU | 2014-02-25 |  | Y | 10 | (yyy), ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DC | Wilkins | 350AXL | 2.5 | H | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 2.5 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 2.5 | VU | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 2.5 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 3 | H | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 3 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 3 | VU | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 3 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 4 | H | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 4 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 4 | VU | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 4 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 6 | H | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 6 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 6 | VU | 2010-04-14 | 2013-04-14 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 6 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 8 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 8 | H | 2010-03-25 | 2013-03-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 8 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 8 | VU | 2010-03-25 | 2013-03-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 10 | H | 2010-03-25 | 2013-03-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350AXL | 10 | VU | 2010-03-25 | 2013-03-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350XL | 0.75 | H | 2006-08-30 | 2012-08-30 | Y | 9 | (iiii) | N
DC | Wilkins | 350XL | 0.75 | VU | 2006-08-30 | 2012-08-30 | Y | 9 | (iiii) | N
DC | Wilkins | 350XL | 1 | H | 2006-10-27 | 2012-10-27 | Y | 9 | (iiii) | N
DC | Wilkins | 350XL | 1 | VU | 2006-10-27 | 2012-10-27 | Y | 9 | (iiii) | N
DC | Wilkins | 350XL | 1.25 | H | 2009-01-08 | 2015-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 1.25 | VU | 2009-01-08 | 2015-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 1.5 | H | 2009-01-08 | 2015-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 1.5 | VU | 2009-01-08 | 2015-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 2 | H | 2009-01-08 | 2015-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 2 | VU | 2009-01-08 | 2015-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 2.5 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
DC | Wilkins | 350XL | 2.5 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 2.5 | VU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
DC | Wilkins | 350XL | 2.5 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 3 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
DC | Wilkins | 350XL | 3 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 3 | VU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
DC | Wilkins | 350XL | 3 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 4 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 4 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 4 | VU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 4 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 6 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 6 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 6 | VU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 6 | VU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 8 | H | 2010-03-25 | 2013-03-25 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 8 | H | 2010-03-25 | 2013-03-25 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 8 | VU | 2010-03-25 | 2013-03-25 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 8 | VU | 2010-03-25 | 2013-03-25 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 350XL | 10 | H | 2010-03-25 | 2013-03-25 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 10 | H | 2010-03-25 | 2013-03-25 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350XL | 10 | VU | 2010-03-25 | 2013-03-25 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
DC | Wilkins | 350XL | 10 | VU | 2010-03-25 | 2013-03-25 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 350XL | 12 | H | 2010-03-25 | 2013-03-25 | Y | 9 | (hh),ssss,tttt,uuuu,vvvv,wwww,xxxx,yyyy,zzzz,aaaaa | N
DC | Wilkins | 450XL | 2.5 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 2.5 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 3 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 3 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 4 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 4 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 6 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 6 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 8 | VUVD | 2010-03-25 | 2013-03-25 | N | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 8 | VUVD | 2010-03-25 | 2013-03-25 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 10 | VUVD | 2010-03-25 | 2013-03-25 | N | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
DC | Wilkins | 450XL | 10 | VUVD | 2010-03-25 | 2013-03-25 | Y | 9 | (hh),ssss,tttt,xxxx,yyyy,zzzz,aaaaa | N
DC | Wilkins | 550 | 0.75 | H | 1976-10-11 | 2012-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1 | H | 1976-10-11 | 2012-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1.25 | H | 1976-10-11 | 2012-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1.5 | H | 1976-10-11 | 2012-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1.5 | H | 1976-10-11 | 2012-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 2 | H | 1976-10-11 | 2012-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 2.5 | H | 1986-09-25 | 2013-09-25 | N | 7 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 3 | H | 1979-08-20 | 2012-08-20 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 4 | H | 1980-06-20 | 2013-06-20 | N | 5 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 6 | H | 1981-07-06 | 2014-07-06 | N | 6 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550A | 0.75 | H | 1987-04-17 | 2014-04-17 | N | 7 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550A | 1 | H | 1987-04-17 | 2014-04-17 | N | 7 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550M | 8 | H | 1989-03-15 | 2013-03-15 | N | 8 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y |  |  | 4"x4"x8" Manifold Formerly MBD
DC | Wilkins | 550M | 10 | H | 1983-04-11 | 2013-04-11 | N | 6 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y |  |  | 6"x6"x10" Manifold Formerly MBD
DC | Wilkins | 950 | 0.75 | H | 1991-07-18 | 2012-07-18 | N | 8 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 1 | H | 1991-07-18 | 2012-07-18 | N | 8 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 1.25 | H | 1991-04-05 | 2015-04-05 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 1.5 | H | 1991-04-05 | 2015-04-05 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 2 | H | 1991-04-05 | 2015-04-05 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 2.5 | H | 1991-11-26 | 2012-11-26 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 3 | H | 1991-11-08 | 2012-11-08 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 950 | 4 | H | 1991-11-08 | 2012-11-08 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 6 | H | 1992-03-18 | 2013-03-18 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 8 | H | 1989-03-18 | 2013-03-18 | N | 8 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
DC | Wilkins | 950A | 0.75 | H | 1991-07-18 | 2012-07-18 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950A | 1 | H | 1991-07-18 | 2012-07-18 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950A | 1.25 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
DC | Wilkins | 950A | 1.5 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
DC | Wilkins | 950A | 2 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
DC | Wilkins | 950XL | 0.75 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo | N
DC | Wilkins | 950XL | 0.75 | VU | 1996-12-12 | 2014-12-12 | N | 8 | (ii),ooo | N
DC | Wilkins | 950XL | 1 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo | N
DC | Wilkins | 950XL | 1.25 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo,ggg | N
DC | Wilkins | 950XL | 1.5 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo | N
DC | Wilkins | 950XL | 2 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),bbb,ooo | N
DC | Wilkins | 950XLD | 0.75 | H | 1999-09-15 | 2014-09-15 | N | 9 | (ii),ooo | N |  |  | Up to Serial # 3863324
DC | Wilkins | 950XLD | 0.75 | H | 1999-09-15 | 2014-09-15 | Y | 9 | (ii),ooo | N |  |  | Starting at Serial # 3863325
DC | Wilkins | 950XLD | 0.75 | H | 2013-07-03 |  | N | 10 | (iiii) | N |  |  | Up to Serial # 3863324
DC | Wilkins | 950XLD | 0.75 | H | 2013-07-03 |  | Y | 10 | (iiii) | N |  |  | Starting at Serial # 3863325
DC | Wilkins | 950XLD | 0.75 | VU | 2000-01-05 | 2014-01-05 | N | 9 | (ii),ooo | N |  |  | Up to Serial # 3863324
DC | Wilkins | 950XLD | 0.75 | VU | 2000-01-05 | 2014-01-05 | Y | 9 | (ii),ooo | N |  |  | Starting at Serial # 3863325
DC | Wilkins | 950XLD | 0.75 | VU | 2013-07-03 |  | N | 10 | (iiii) | N |  |  | Up to Serial # 3863324
DC | Wilkins | 950XLD | 0.75 | VU | 2013-07-03 |  | Y | 10 | (iiii) | N |  |  | Starting at Serial # 3863325
DC | Wilkins | 950XLT | 0.75 | H | 1997-05-09 | 2015-05-09 | N | 9 | (ii),ooo | N
DC | Wilkins | 950XLT | 1 | H | 1997-05-09 | 2015-05-09 | N | 9 | (ii),ooo | N
DC | Wilkins | 950XLT | 1.25 | H | 1998-06-19 | 2013-06-19 | N | 9 | (ii),ooo | N
DC | Wilkins | 950XLT | 1.5 | H | 1998-04-09 | 2013-04-09 | N | 9 | (ii),ooo | N
DC | Wilkins | 950XLT | 2 | H | 1998-04-09 | 2013-04-09 | N | 9 | (ii),ooo,bbbbb,ccccc | N
DC | Wilkins | 950XLT2 | 0.75 | H | 2009-08-21 | 2012-08-21 | Y | 9 | (iiii) | N
DC | Wilkins | 950XLT2 | 1 | H | 2009-08-21 | 2012-08-21 | Y | 9 | (iiii) | N
DC | Wilkins | 950XLT2 | 1.25 | H | 2009-08-21 | 2012-08-21 | Y | 9 | (iiii) | N
DC | Wilkins | 950XLT2 | 1.5 | H | 2009-08-21 | 2012-08-21 | Y | 9 | (iiii) | N
DC | Wilkins | 950XLT2 | 2 | H | 2009-08-21 | 2012-08-21 | Y | 9 | (iiii) | N
DC | Wilkins | 950XLT2U | 0.75 | H | 2011-02-22 | 2014-02-22 | Y | 9 | (mmmmm) | N
DC | Wilkins | 950XLTBF | 2 | H | 2011-02-22 | 2014-02-22 | N | 9 | (bbbbb) | N
DC | Wilkins | 950XLTBFSS | 2 | H | 2011-02-22 | 2014-02-22 | N | 9 | (ccccc) | N
DC | Wilkins | 950XLTU | 0.75 | H | 2006-08-14 | 2012-08-14 | N | 9 | (ggg),xxx | N
DC | Wilkins | 950XLTU | 1 | H | 2006-08-14 | 2012-08-14 | N | 9 | (ggg),xxx | N
DC | Wilkins | 950XLU | 0.75 | H | 1994-02-15 | 2015-02-15 | N | 8 | (ggg),xxx | N
DC | Wilkins | 950XLU | 1 | H | 1994-02-15 | 2015-02-15 | N | 8 | (ggg),xxx | N
DC | Wilkins | 950XLU | 1.5 | H | 1994-02-15 | 2015-02-15 | N | 8 | (ggg),xxx | N
DC | Wilkins | 950XLU | 2 | H | 1994-02-15 | 2015-02-15 | N | 8 | (ggg),xxx | N
DC | Wilkins | MBD | 8 | [9 empty] | 4"x4"x8" Manifold, Model designation changed to 550M
DC | Wilkins | MBD | 10 | [9 empty] | 6"x6"x10" Manifold, Model designation changed to 550M
DC | Wilkins | 350D | 0.75 | H | 2009-05-19 | 2015-05-19 | N | 9 | (ii), ooo | N
DC | Wilkins | 350D | 0.75 | VU | 2009-06-22 | 2012-06-22 | N | 9 | (ii), ooo | N
DCDA | Ames | 3000-1SS | 12 | VU | 2011-02-22 | 2014-02-22 | N | 9 | (mm), ll | N | Ames 200B 3/4" (VU); Watts 719QT 3/4" (VU) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000-1SS | 12 | H | 2009-12-04 | 2012-12-04 | N | 9 | (mm), ll | N | Ames 200B 3/4" (H); Watts 719QT 3/4" (H) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000B | 2 | H | 1997-06-16 | 2012-06-16 | N | 9 | (bbb),jjjj,rrrrr | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000B | 2 | VU | 1997-06-16 | 2012-06-16 | N | 9 | (bbb),jjjj,rrrrr | N | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000B-FP | 2 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000BM1 | 2 | H | 2012-06-19 |  | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000BM1 | 2 | VU | 2012-06-19 |  | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000CIV | 4 | H | 1987-07-27 | 2014-07-27 | N | 6 | (pp),hh,uu,eee | N | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000CIV | 4 | VU | 1996-08-27 | 2014-08-27 | N | 8 | (pp),hh,uu,eee | N | Ames 2000B 1/2"(VU),Watts 007QT 1/2"(VU) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000CIV | 6 | H | 1987-07-27 | 2014-07-27 | N | 6 | (pp),hh,uu,eee | N | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000CIV | 6 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (pp),hh,mm,uu,eee | N | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000CIV | 8 | H | 1987-04-19 | 2014-04-19 | N | 6 | (pp),hh,mm,uu,eee | N | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000CIV | 8 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (pp),hh,mm,uu,eee | N | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000CIV | 10 | H | 1987-07-27 | 2014-07-27 | N | 6 | (pp),hh,mm,uu,eee | N | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),E,F,G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000CIV | 10 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (pp),hh,mm,uu,eee | N | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Ames | 3000DCDA | 4 | H | 1988-01-11 | 2015-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDA
DCDA | Ames | 3000DCDA | 6 | H | 1988-01-11 | 2015-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDA-I
DCDA | Ames | 3000DCDA | 8 | H | 1988-01-11 | 2015-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDA
DCDA | Ames | 3000DCDC | 10 | H | 1987-08-04 | 2014-08-04 | N | 7 | (uu),ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H),Watts 709QT 3/4" (H), Ames 2000B 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDA
DCDA | Ames | 3000GDCDA | 4 | H | 1988-01-11 | 2015-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDA
DCDA | Ames | 3000GDCDA | 6 | H | 1988-01-11 | 2015-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDA-I
DCDA | Ames | 3000GDCDA | 8 | H | 1988-01-11 | 2015-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDA
DCDA | Ames | 3000GDCDC | 10 | H | 1987-08-04 | 2014-08-04 | N | 7 | uu,ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly DCDC
DCDA | Ames | 3000SE | 2.5 | H | 1996-09-10 | 2014-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),N,O,P,Q
DCDA | Ames | 3000SE | 6 | H | 1995-05-24 | 2013-05-24 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SE | 8 | H | 1992-09-09 | 2013-09-09 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SEA | 8 | H | 1995-05-05 | 2013-05-05 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Ames 2000SS 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SEWM1 | 6 | H | 1993-11-22 | 2014-11-22 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | 3000SS | 2.5 | H | 1995-05-24 | 2013-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SS | 2.5 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SEWM1
DCDA | Ames | 3000SS | 3 | H | 1995-05-24 | 2013-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SS | 3 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SEWM1
DCDA | Ames | 3000SS | 4 | H | 1995-05-24 | 2013-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SS | 4 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SEWM1
DCDA | Ames | 3000SS | 6 | H | 1992-09-09 | 2013-09-09 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SS | 6 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SEWM1
DCDA | Ames | 3000SS | 8 | H | 1996-09-16 | 2014-09-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SS | 10 | H | 2001-02-16 | 2013-02-16 | N | 8 | (ll),mm,oo,pp,ffff,gggg | N | Ames 2000B 3/4" (H) | (J),C,E,F,G,H,I,K,L,M,N,O,P,Q
DCDA | Ames | 3000SS | 12 | VU | 2011-02-22 | 2014-02-22 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (VU) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000SS | 12 | H | 2009-12-04 | 2012-12-04 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000SSA | 6 | H | 1995-05-05 | 2013-05-05 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Ames 2000SS 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Ames | 3000SSM | 4 | H | 1995-05-05 | 2013-05-05 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Ames 2000SS 1" (H) | (R)
DCDA | Ames | 3000SSM | 6 | H | 1995-05-05 | 2013-05-05 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 1 1/2" (H) | (S)
DCDA | Ames | 3000SSWM1 | 2.5 | H | 1991-07-11 | 2012-07-11 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | 3000SSWM1 | 3 | H | 1991-07-11 | 2012-07-11 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | 3000SSWM1 | 4 | H | 1991-07-11 | 2012-07-11 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | Colt 300aBF | 2.5 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aBF | 2.5 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aBF | 3 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aBF | 3 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aBF | 4 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aBF | 4 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aBF | 6 | H | 2004-09-29 | 2013-09-29 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300aBF | 6 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Colt 300aGV | 2.5 | H | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aGV | 2.5 | VU | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aGV | 3 | H | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aGV | 3 | VU | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aGV | 4 | H | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aGV | 4 | VU | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300aGV | 6 | H | 2004-11-03 | 2013-11-03 | N | 9 | (zzz) | N | Ames 2000BM3 3/4 (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300aGV | 6 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Colt 300BF | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 4 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 4 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 6 | H | 2007-03-02 | 2013-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 6 | VU | 2007-03-02 | 2013-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 8 | H | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Colt 300BF | 8 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Colt 300BF | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300BF | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 4 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 4 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 6 | H | 2007-03-02 | 2013-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 6 | VU | 2007-03-02 | 2013-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 8 | H | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Colt 300GV | 8 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Colt 300GV | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300GV | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Colt 300NBF | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NBF | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NBF | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NBF | 6 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NBF | 8 | VUVD | 2013-01-03 |  | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NBF | 10 | VUVD | 2013-05-28 |  | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NGV | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NGV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NGV | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NGV | 6 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NGV | 8 | VUVD | 2013-01-03 |  | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NGV | 10 | VUVD | 2013-05-28 |  | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | DCDA | 4 | [9 empty] | model designation changed to 3000DCDA
DCDA | Ames | DCDA | 4 | [9 empty] | model designation changed to 3000GDCDA
DCDA | Ames | DCDA | 8 | [9 empty] | model designation changed to 3000DCDA
DCDA | Ames | DCDA | 8 | [9 empty] | model designation changed to 3000GDCDA
DCDA | Ames | DCDA | 10 | [9 empty] | model designation changed to 3000DCDC
DCDA | Ames | DCDA-I | 6 | [9 empty] | model designation changed to 3000DCDA
DCDA | Ames | DCDA-I | 6 | [9 empty] | model designation changed to 3000GDCDA
DCDA | Ames | DCDC | 4 | H | 1985-06-14 | 2012-06-14 | N | 6 | ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q
DCDA | Ames | DCDC | 6 | H | 1985-06-14 | 2012-06-14 | N | 6 | ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q
DCDA | Ames | DCDC | 8 | H | 1987-08-04 | 2014-08-04 | N | 7 | ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q
DCDA | Ames | DCDC | 10 | [9 empty] | model designation changed to 3000GDCDC
DCDA | Ames | LFColt 300BF | 2.5 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 2.5 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 3 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 3 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 4 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 4 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 6 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 6 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 8 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 8 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 10 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 10 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 2.5 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 2.5 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 3 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 3 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 4 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 4 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 6 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 6 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 8 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 8 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 10 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 10 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 4 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 6 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 8 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 10 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 6 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 8 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 10 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 2.5 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 2.5 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 3 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 3 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 4 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 4 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 6 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 6 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 8 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 8 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 10 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 10 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 2.5 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 2.5 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 3 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 3 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 4 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 4 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 6 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 6 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 8 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 8 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 10 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 10 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 4 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 6 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 8 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 10 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 6 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 8 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 10 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | Maxim 300aBF | 2.5 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aBF | 2.5 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aBF | 3 | H | 2003-10-06 | 2012-10-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aBF | 3 | VU | 2003-10-06 | 2012-10-06 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aBF | 4 | H | 2004-11-03 | 2013-11-03 | N | 9 | (yyy) | N | Ames 2000BM3 3/4 (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300aBF | 4 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Maxim 300aGV | 2.5 | H | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aGV | 2.5 | VU | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aGV | 3 | H | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aGV | 3 | VU | 2003-10-06 | 2012-10-06 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300aGV | 4 | H | 2004-11-03 | 2013-11-03 | N | 9 | (zzz) | N | Ames 2000BM3 3/4 (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300aGV | 4 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Maxim 300BF | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 4 | H | 2007-03-02 | 2013-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 4 | Vu | 2007-03-02 | 2013-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 6 | H | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Maxim 300BF | 6 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Ames | Maxim 300BF | 8 | H | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 8 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300BF | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 4 | H | 2007-03-02 | 2013-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 4 | VU | 2007-03-02 | 2013-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 6 | H | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,IJ,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300GV | 6 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,IJ,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300GV | 8 | H | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 8 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300GV | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Ames | Maxim 300NBF | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NBF | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NBF | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NBF | 6 | VUVD | 2013-01-03 |  | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NBF | 8 | VUVD | 2013-05-28 |  | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NBF | 10 | VUVD | 2013-05-28 |  | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 6 | VUVD | 2013-01-03 |  | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 8 | VUVD | 2013-05-28 |  | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 10 | VUVD | 2013-05-28 |  | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Apollo/Conbraco | 4060003 | 3 | [9 empty] | model designation changed to 40600000
DCDA | Apollo/Conbraco | 4060003 | 3 | [9 empty] | model designation changed to 40600C3
DCDA | Apollo/Conbraco | 40600000 | 3 | H | 1996-08-20 | 2014-08-20 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060003
DCDA | Apollo/Conbraco | 10DCDA | 10 | [9 empty] | model designation changed to DCDA4S
DCDA | Apollo/Conbraco | 10DCDA | 10 | [9 empty] | model designation changed to DCDA4S
DCDA | Apollo/Conbraco | 2 1/2DCDA | 2.5 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDA | 2.5 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDA6 | 2.5 | H | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDA6 | 2.5 | VU | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDA7 | 2.5 | H | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDA7 | 2.5 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDA8 | 2.5 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDA8 | 2.5 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 2 1/2DCDAU | 2.5 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA | 3 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA | 3 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA6 | 3 | H | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA6 | 3 | VU | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA7 | 3 | H | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA7 | 3 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA8 | 3 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDA8 | 3 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 3DCDAU | 3 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 40600C3 | 3 | H | 1996-08-20 | 2014-08-20 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060003
DCDA | Apollo/Conbraco | 4060A03 | 4 | [9 empty] | model designation changed to 4060AC3
DCDA | Apollo/Conbraco | 4060A03 | 4 | [9 empty] | model designation changed to 4060AE3
DCDA | Apollo/Conbraco | 4060AC3 | 4 | H | 1993-04-13 | 2014-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060A03
DCDA | Apollo/Conbraco | 4060AC6 | 4 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4060AE3 | 4 | H | 1993-04-13 | 2014-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060A03
DCDA | Apollo/Conbraco | 4060AE6 | 4 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4060C03 | 6 | [9 empty] | model designation changed to 4060CC3
DCDA | Apollo/Conbraco | 4060C03 | 6 | [9 empty] | model designation changed to 4060CE3
DCDA | Apollo/Conbraco | 4060CC3 | 6 | H | 1993-06-02 | 2014-06-02 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060C03
DCDA | Apollo/Conbraco | 4060CC6 | 6 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4060CE3 | 6 | H | 1993-06-02 | 2014-06-02 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060C03
DCDA | Apollo/Conbraco | 4060CE6 | 6 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4060E03 | 8 | [9 empty] | model designation changed to 4060EC3
DCDA | Apollo/Conbraco | 4060E03 | 8 | [9 empty] | model designation changed to 4060EE3
DCDA | Apollo/Conbraco | 4060EC3 | 8 | H | 1993-04-13 | 2014-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060E03
DCDA | Apollo/Conbraco | 4060EC6 | 8 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4060EE3 | 8 | H | 1993-04-13 | 2014-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060E03
DCDA | Apollo/Conbraco | 4060EE6 | 8 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4060G03 | 10 | [9 empty] | model designation changed to 4060GC3
DCDA | Apollo/Conbraco | 4060G03 | 10 | [9 empty] | model designation changed to 4060GE3
DCDA | Apollo/Conbraco | 4060GC3 | 10 | H | 1993-04-13 | 2014-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060G03
DCDA | Apollo/Conbraco | 4060GC6 | 10 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4060GE3 | 10 | H | 1993-04-12 | 2014-03-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4060G03
DCDA | Apollo/Conbraco | 4060GE6 | 10 | H | 2000-02-01 | 2015-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA | 4 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA | 4 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA6 | 4 | H | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA6 | 4 | VU | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA7 | 4 | H | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA7 | 4 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA8 | 4 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDA8 | 4 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4DCDAU | 4 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 4SG 600U | 2.5 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 3 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 4 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 6 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 8 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG-600 | 2.5 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 2.5 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 3 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 3 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 4 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 4 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 6 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 6 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 8 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 8 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 6DCDA | 6 | H | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDA | 6 | VU | 2000-10-16 | 2012-10-16 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDA6 | 6 | H | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDA6 | 6 | VU | 2001-04-10 | 2013-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDA7 | 6 | H | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDA7 | 6 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDA8 | 6 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDA8 | 6 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 6DCDAU | 6 | VUVD | 2001-04-10 | 2013-04-10 | N | 9 | (ll),mm | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 8DCDA | 8 | H | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 8DCDA | 8 | VU | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 8DCDA7 | 8 | H | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 8DCDA7 | 8 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 8DCDA8 | 8 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | 8DCDA8 | 8 | VU | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Apollo/Conbraco | DCDA4S | 10 | H | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),F,G,H,I,J,K,L,N,O,P,Q | formerly 10DCDA
DCDA | Apollo/Conbraco | DCDA4S | 10 | VU | 2003-01-16 | 2015-01-16 | N | 9 | (mm),ll | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),F,G,H,I,J,K,L,N,O,P,Q | formerly 10DCDA
DCDA | Apollo/Conbraco | DCDA4SG | 2.5 | H | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 2.5 | VU | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 3 | H | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 3 | VU | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 4 | H | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 4 | VU | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 6 | H | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 6 | VU | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 8 | H | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 8 | VU | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SGN | 2.5 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 3 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 4 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 6 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 8 | VUVD | 2007-10-18 | 2013-10-18 | N | 9 | (yyy)ppp,qqq,ttt | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,M,N,O,P,Q | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDALF4A | 2.5 | H | 2013-10-30 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 2.5 | VU | 2013-10-30 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 3 | H | 2013-10-30 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 3 | VU | 2013-10-30 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 4 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 4 | VU | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 6 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 6 | VU | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 8 | H | 2014-05-15 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4A | 8 | VU | 2014-05-15 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4AN | 2.5 | VUVD | 2014-06-10 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4AN | 3 | VUVD | 2014-04-08 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4AN | 4 | VUVD | 2014-01-23 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4AN | 6 | VUVD | 2014-06-10 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
DCDA | Apollo/Conbraco | DCDALF4AN | 8 | VUVD | 2014-03-14 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
DCDA | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
DCDA | Febco | 856 | 2.5 | H | 1997-03-19 | 2015-03-19 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 2.5 | VU | 2000-01-05 | 2014-01-05 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 3 | H | 1997-03-19 | 2015-03-19 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 3 | VU | 2000-01-05 | 2014-01-05 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 4 | H | 1994-05-04 | 2015-05-04 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 4 | VU | 1996-04-16 | 2014-04-16 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 6 | H | 1994-05-04 | 2015-05-04 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 6 | VU | 1996-04-16 | 2014-04-16 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 8 | H | 1995-10-04 | 2013-10-04 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 856 | 8 | VU | 2000-01-05 | 2014-01-05 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | N | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 858 | 2 | H | 2006-08-01 | 2012-08-01 | N | 9 | bbb,jjjj | N | Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Febco | 858 | 2 | VU | 2006-08-01 | 2012-08-01 | N | 9 | bbb,jjjj | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Febco | 858 | 2.5 | H | 2006-08-01 | 2012-08-01 | N | 8 | (pp), gg, hh,ll, mm, oo, tt, uu, zz, fff | N | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Febco | 858 | 2.5 | VU | 2006-08-01 | 2012-08-01 | N | 8 | (pp), gg, hh,ll, mm, oo, tt, uu, zz, fff | N | Watts 007M2QT 3/4" (VU) | (H),D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Febco | 858 | 3 | H | 2006-08-01 | 2012-08-01 | N | 8 | (pp), gg, hh,ll, mm, oo, tt, uu, zz, fff | N | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Febco | 876 | 2.5 | VUVD | 1995-03-10 | 2013-03-10 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876 | 3 | VUVD | 1995-03-10 | 2013-03-10 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876 | 4 | VUVD | 1994-05-04 | 2015-05-04 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876 | 6 | VUVD | 1994-05-04 | 2015-05-04 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876 | 8 | VUVD | 1995-05-24 | 2013-05-24 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876 | 10 | VUVD | 1996-10-04 | 2014-10-04 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 806 Type YD | 3 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 4 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 6 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 8 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 10 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806YD | 3 | H | 1988-09-26 | 2012-09-26 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 806 Type YD
DCDA | Febco | 806YD | 4 | H | 1987-07-10 | 2014-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q | formerly 806 Type YD
DCDA | Febco | 806YD | 6 | H | 1987-07-10 | 2014-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q | formerly 806 Type YD
DCDA | Febco | 806YD | 8 | H | 1987-07-10 | 2014-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q | formerly 806 Type YD
DCDA | Febco | 806YD | 10 | H | 1987-07-10 | 2014-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q | formerly 806 Type YD
DCDA | Febco | 856ST | 2.5 | H | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 2.5 | VU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (VU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 3 | H | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 3 | VU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (VU) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 4 | H | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 4 | VU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (VU) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 6 | H | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 6 | VU | 2012-08-09 |  | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 8 | H | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 8 | VU | 2012-08-09 |  | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 10 | H | 2013-09-03 |  | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 10 | VU | 2013-09-03 |  | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876V | 2.5 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 2.5 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 3 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 3 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 4 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 4 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 6 | VUVD | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 6 | VUVU | 1996-03-08 | 2014-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 8 | VUVD | 1997-01-06 | 2014-01-06 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 8 | VUVU | 1997-01-06 | 2014-01-06 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 10 | VUVD | 1997-07-11 | 2012-07-11 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876V | 10 | VUVU | 1997-07-11 | 2012-07-11 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Febco | 876VST | 2.5 | VUVD | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 2.5 | VUVU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 3 | VUVD | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 3 | VUVU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 4 | VUVD | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 4 | VUVU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 6 | VUVD | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 6 | VUVU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 8 | VUVD | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 8 | VUVU | 2012-05-22 | 2015-05-22 | N | 9 | (ll), mm | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Watts | 007DCDA | 2 | H | 1997-06-16 | 2012-06-16 | N | 9 | (bbb),jjjj,rrrrr | N | Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q | Previously Approved 8th Ed. (19 Apr 1996)
DCDA | Watts | 007DCDA | 2 | VU | 1997-06-16 | 2012-06-16 | N | 9 | (bbb),jjjj,rrrrr | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q | Previously Approved 8th Ed. (10 Sept 1996)
DCDA | Watts | 007DCDA | 2.5 | H | 1993-10-11 | 2014-10-11 | N | 8 | (pp),gg,hh,ll,mm,oo,tt,uu,zz,ffff,gggg | N | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 007DCDA | 2.5 | VU | 1996-08-27 | 2014-08-27 | N | 8 | (pp),gg,hh,ll,mm,oo,tt,uu,zz,ffff,gggg | N | Watts 007M2QT 3/4" (VU) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 007DCDA | 3 | H | 1992-09-19 | 2013-09-19 | N | 8 | (pp),hh,mm,uu,zz,ffff,gggg | N | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 007DCDA-FP | 2 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 007M1DCDA | 2 | H | 2012-06-19 |  | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 007M1DCDA | 2 | VU | 2012-06-19 |  | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 709DCDA | 3 | H | 1987-04-19 | 2014-04-19 | N | 6 | (pp),hh,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q | formerly 709DDC
DCDA | Watts | 709DCDA | 4 | H | 1987-07-27 | 2014-07-27 | N | 6 | (pp),hh,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q | formerly 709DDC
DCDA | Watts | 709DCDA | 4 | VU | 1996-08-27 | 2014-08-27 | N | 8 | (pp),hh,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (VU), Watts 007M2QT 3/4" (VU) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q | formerly 709DDC
DCDA | Watts | 709DCDA | 6 | H | 1987-07-27 | 2014-07-27 | N | 6 | (pp),hh,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q | formerly 709DDC
DCDA | Watts | 709DCDA | 6 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 709DCDA | 8 | H | 1987-04-19 | 2014-04-19 | N | 6 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q | formerly 709DDC
DCDA | Watts | 709DCDA | 8 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 709DCDA | 10 | H | 1987-07-27 | 2014-07-27 | N | 6 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),E,F,G,H,I,J,K,L,M,O,P,Q | formerly 709DDC
DCDA | Watts | 709DCDA | 10 | VU | 1996-12-05 | 2014-12-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 709DDC | 3 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 4 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 4 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 6 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 8 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 10 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 757aDCDABF | 2.5 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDABF | 2.5 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDABF | 3 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDABF | 3 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDABF | 4 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDABF | 4 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDABF | 6 | H | 2004-11-03 | 2013-11-03 | N | 9 | (yyy) | N | Watts 007M3QT 3/4 (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757aDCDABF | 6 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757aDCDAGV | 2.5 | H | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDAGV | 2.5 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDAGV | 3 | H | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDAGV | 3 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDAGV | 4 | H | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDAGV | 4 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757aDCDAGV | 6 | H | 2005-01-18 | 2014-01-18 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757aDCDAGV | 6 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDABF | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDABF | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDABF | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDABF | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDABF | 4 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDABF | 4 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDABF | 6 | H | 2007-03-19 | 2013-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H ) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDABF | 6 | VU | 2007-03-19 | 2013-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDABF | 8 | H | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDABF | 8 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDABF | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDABF | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 4 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 4 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 6 | H | 2007-03-19 | 2013-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H ) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDAGV | 6 | VU | 2007-03-19 | 2013-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDAGV | 8 | H | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDAGV | 8 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 757DCDAGV | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757DCDAGV | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 757NDCDABF | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDABF | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDABF | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDABF | 6 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDABF | 8 | VUVD | 2013-01-03 |  | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDABF | 10 | VUVD | 2013-05-28 |  | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDAGV | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDAGV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDAGV | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDAGV | 6 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDAGV | 8 | VUVD | 2013-01-03 |  | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDAGV | 10 | VUVD | 2013-05-28 |  | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767aDCDABF | 2.5 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDABF | 2.5 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDABF | 3 | H | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDABF | 3 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDABF | 4 | H | 2006-08-30 | 2012-08-30 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767aDCDABF | 4 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767aDCDAGV | 2.5 | H | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDAGV | 2.5 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDAGV | 3 | H | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDAGV | 3 | VU | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767aDCDAGV | 4 | VU | 2005-01-18 | 2014-01-18 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767aDCDAGV | 4 | H | 2003-11-06 | 2012-11-06 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 4 | H | 2007-03-19 | 2013-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H ) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDABF | 4 | VU | 2007-03-19 | 2013-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDABF | 6 | H | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDABF | 6 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDABF | 8 | H | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 8 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDABF | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 2.5 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 2.5 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 3 | H | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 3 | VU | 2005-10-04 | 2014-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 4 | H | 2007-03-19 | 2013-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H ) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDAGV | 4 | VU | 2007-03-19 | 2013-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDAGV | 6 | H | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDAGV | 6 | VU | 2007-03-09 | 2013-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N), G, H, I J, K L, M, N, O, P, Q
DCDA | Watts | 767DCDAGV | 8 | H | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 8 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767DCDAGV | 10 | VU | 2009-09-17 | 2012-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 767NDCDABF | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDABF | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDABF | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDABF | 6 | VUVD | 2013-01-03 |  | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDABF | 8 | VUVD | 2013-05-28 |  | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDABF | 10 | VUVD | 2013-05-28 |  | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 6 | VUVD | 2013-01-03 |  | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 8 | VUVD | 2013-05-28 |  | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 10 | VUVD | 2013-05-28 |  | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 770DCDA | 4 | H | 1992-05-20 | 2013-05-20 | N | 8 | pp,hh,mm,uu,zz | Y | Watts 007M1QT 3/4" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 770DCDA | 8 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu | Y | Watts 007M1QT 3/4" (H) | (N),D,E,F,G,H,I,J,K,L,M,O,P,Q
DCDA | Watts | 772DCDA | 4 | H | 1992-08-01 | 2013-08-01 | N | 8 | oo | Y | Watts 007M1QT 3/4" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 772DCDA | 10 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo | Y | Watts 007M1QT 3/4" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 774DCDA | 2.5 | H | 1995-05-24 | 2013-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Watts | 774DCDA | 3 | H | 1995-05-24 | 2013-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Watts | 774DCDA | 4 | H | 1995-05-24 | 2013-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Watts | 774DCDA | 6 | H | 1992-09-09 | 2013-09-09 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Watts | 774DCDA | 8 | H | 1996-09-16 | 2014-09-16 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Watts | 774DCDA | 10 | H | 2001-02-16 | 2013-02-16 | N | 8 | (ll),mm,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (J),C,E,F,G,H,I,K,L,M,N,O,P,Q
DCDA | Watts | 774DCDA | 12 | H | 2010-02-18 | 2013-02-18 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (H); Watts 007M3QT 3/4" (H) | (N),H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774DCDA | 12 | VU | 2011-03-21 | 2014-03-21 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (H); Watts 007M3QT 3/4" (H) | (N),H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774DCDA-1 | 12 | H | 2010-02-18 | 2013-02-18 | N | 9 | (mm), ll | N | Ames 200B 3/4" (H); Watts 719QT 3/4" (H) | (N),H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774DCDA-1 | 12 | VU | 2011-03-21 | 2014-03-21 | N | 9 | (mm), ll | N | Ames 200B 3/4" (VU); Watts 719QT 3/4" (VU) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774XDCDA | 2.5 | H | 1996-09-10 | 2014-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),N,O,P,Q
DCDA | Watts | 774XDCDA | 6 | H | 1995-05-24 | 2013-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,uu,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Watts | 774XDCDA | 8 | H | 1992-09-09 | 2013-09-09 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Watts | LF757DCDABF | 2.5 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 2.5 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 3 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 3 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 4 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 4 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 6 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 6 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 8 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 8 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 10 | H | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 10 | VU | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 2.5 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 2.5 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 3 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 3 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 4 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 4 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 6 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 6 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 8 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 8 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 10 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 10 | VU | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 4 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 6 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 8 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 10 | VUVD | 2014-01-08 |  | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 6 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 8 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 10 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 2.5 | H | 2005-06-22 | 2014-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ADA | 2.5 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 2.5 | VU | 2005-06-22 | 2014-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ADA | 2.5 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 3 | H | 2005-06-22 | 2014-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ADA | 3 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 3 | VU | 2005-06-22 | 2014-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ADA | 3 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 4 | H | 2004-03-16 | 2013-03-16 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 350ADA | 4 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 4 | VU | 2004-03-16 | 2013-03-16 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 350ADA | 4 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 6 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 6 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 6 | H | 2003-11-25 | 2012-11-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 350ADA | 6 | VU | 2003-11-25 | 2012-11-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 350ADA | 8 | H | 2004-02-12 | 2013-02-12 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q
DCDA | Wilkins | 350ADA | 8 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 8 | VU | 2004-02-12 | 2013-02-12 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q
DCDA | Wilkins | 350ADA | 8 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 10 | H | 2006-04-06 | 2015-04-06 | N | 9 | (qqq),ttt,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N), F, G, H, I J, K L, M, N, O, P, Q
DCDA | Wilkins | 350ADA | 10 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 10 | VU | 2006-04-06 | 2015-04-06 | N | 9 | (qqq),ttt,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (N), F, G, H, I J, K L, M, N, O, P, Q
DCDA | Wilkins | 350ADA | 10 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 2.5 | H | 2010-06-16 | 2013-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DCDA | Wilkins | 350ADAR | 2.5 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 2.5 | VU | 2010-06-16 | 2013-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DCDA | Wilkins | 350ADAR | 2.5 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 3 | H | 2010-06-16 | 2013-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DCDA | Wilkins | 350ADAR | 3 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 3 | VU | 2010-06-16 | 2013-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DCDA | Wilkins | 350ADAR | 3 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 4 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DCDA | Wilkins | 350ADAR | 4 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 4 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DCDA | Wilkins | 350ADAR | 4 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 6 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DCDA | Wilkins | 350ADAR | 6 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 6 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DCDA | Wilkins | 350ADAR | 6 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 8 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86"
DCDA | Wilkins | 350ADAR | 8 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 8 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86"
DCDA | Wilkins | 350ADAR | 8 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 10 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
DCDA | Wilkins | 350ADAR | 10 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 10 | VU | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
DCDA | Wilkins | 350ADAR | 10 | VU | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 2.5 | H | 2013-04-18 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 2.5 | H | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 2.5 | VU | 2013-04-18 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 2.5 | VU | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 3 | H | 2013-04-18 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 3 | H | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 3 | VU | 2013-04-18 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 3 | VU | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 4 | H | 2013-04-18 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),F, G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 4 | H | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 4 | VU | 2013-04-18 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (N),F, G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 4 | VU | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 6 | H | 2013-07-03 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 6 | H | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 6 | VU | 2013-07-03 |  | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (N),G,H,I,J,K,L,M,N,O,P,Q
DCDA | Wilkins | 350ASTDA | 6 | VU | 2014-02-18 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 8 | H | 2014-02-20 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 8 | VU | 2014-02-20 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 10 | H | 2014-02-20 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 10 | VU | 2014-02-20 |  | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDAR | 2.5 | H | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
DCDA | Wilkins | 350ASTDAR | 2.5 | VU | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
DCDA | Wilkins | 350ASTDAR | 3 | H | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
DCDA | Wilkins | 350ASTDAR | 3 | VU | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
DCDA | Wilkins | 350ASTDAR | 4 | H | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
DCDA | Wilkins | 350ASTDAR | 4 | VU | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
DCDA | Wilkins | 350ASTDAR | 6 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
DCDA | Wilkins | 350ASTDAR | 6 | VU | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
DCDA | Wilkins | 350ASTDAR | 8 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DCDA | Wilkins | 350ASTDAR | 8 | VU | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DCDA | Wilkins | 350ASTDAR | 10 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DCDA | Wilkins | 350ASTDAR | 10 | VU | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DCDA | Wilkins | 350DA | 2.5 | H | 2002-04-03 | 2014-04-03 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 2.5 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 2.5 | VU | 2002-10-08 | 2014-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 2.5 | VU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | H | 2002-04-03 | 2014-04-03 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 3 | H | 2002-04-03 | 2014-04-03 | Y | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | VU | 2002-10-08 | 2014-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 3 | VU | 2002-10-08 | 2014-10-08 | Y | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | VU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | H | 1999-09-15 | 2014-09-15 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 4 | H | 1999-09-15 | 2014-09-15 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | VU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | VU | 2000-09-09 | 2012-09-09 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 4 | VU | 2000-09-09 | 2012-09-09 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | H | 1999-10-18 | 2014-10-18 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 6 | H | 1999-10-18 | 2014-10-18 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | VU | 2000-01-05 | 2014-01-05 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 6 | VU | 2000-01-05 | 2014-01-05 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | VU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | H | 2002-07-03 | 2014-07-03 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 8 | H | 2002-07-03 | 2014-07-03 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | VU | 2003-01-16 | 2015-01-16 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 8 | VU | 2003-01-16 | 2015-01-16 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | VU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | H | 2002-08-28 | 2014-08-28 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 10 | H | 2002-08-28 | 2014-08-28 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | VU | 2003-03-14 | 2015-03-14 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 10 | VU | 2003-03-14 | 2015-03-14 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy.zzzz,kkkkk | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | VU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 12 | H | 2014-02-18 |  | Y | 9 | (hh),vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (O) | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 12 | H | 2009-10-20 | 2012-10-20 | N | 9 | (hh),vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q | Up to Serial # N4230
DCDA | Wilkins | 350DA | 12 | H | 2009-10-20 | 2012-10-20 | Y | 9 | (hh),ssss,tttt,uuuu,vvvv,wwww,xxxx,yyyy,zzzz,aaaaa | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 4 | VUVD | 2000-04-12 | 2015-04-12 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 450DA | 4 | VUVD | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 6 | VUVD | 2000-05-24 | 2015-05-24 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 450DA | 6 | VUVD | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 8 | VUVD | 2004-08-03 | 2013-08-03 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q
DCDA | Wilkins | 450DA | 8 | VUVD | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 10 | VUVD | 2004-08-03 | 2013-08-03 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q
DCDA | Wilkins | 450DA | 10 | VUVD | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 950DA | 2.5 | H | 1994-01-02 | 2014-01-02 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | N | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 2.5 | VU | 1996-12-12 | 2014-12-12 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | N | Wilkins 950XL 3/4" (VU) | (M),D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 3 | H | 1994-01-02 | 2014-01-02 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | N | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 3 | VU | 1996-12-12 | 2014-12-12 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | N | Wilkins 950XL 3/4" (VU) | (M),D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 4 | H | 1993-06-09 | 2014-06-09 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 4 | VU | 1996-12-12 | 2014-12-12 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 6 | H | 1993-06-09 | 2014-06-09 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 6 | VU | 1996-12-12 | 2014-12-12 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (VU) | (M),D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 8 | H | 1993-06-09 | 2014-06-09 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy.zzzz | N | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 8 | VU | 1996-12-12 | 2014-12-12 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy.zzzz | N | Wilkins 950XL 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950DA | 10 | H | 1994-06-23 | 2012-06-23 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy.zzzz | N | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | 950XLTDA | 2 | H | 2009-05-19 | 2015-05-19 | N | 9 | (bbb) | N | Wilkins 350D 3/4" (H) | (N), F, G, H, I J, K L, M, N, O, P, Q
DCDA | Wilkins | 950XLTDA | 2 | VU | 2009-06-22 | 2012-06-22 | N | 9 | (bbb) | N | Wilkins 350D 3/4" (VU) | (N), F, G, H, I J, K L, M, N, O, P, Q
DCDA | Wilkins | 950XLTDABF | 2 | H | 2009-05-19 | 2015-05-19 | N | 9 | (bbbbb), ccccc | N | Wilkins 350D 3/4" (H) | (N), F, G, H, I J, K L, M, N, O, P, Q
DCDA | Wilkins | 950XLTDABF | 2 | VU | 2009-06-22 | 2012-06-22 | N | 9 | (bbbbb), ccccc | N | Wilkins 350D 3/4" (VU) | (N), F, G, H, I J, K L, M, N, O, P, Q
DCDA | Wilkins | DCDA | 2.5 | H | 1987-03-05 | 2014-03-05 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | DCDA | 3 | H | 1987-03-05 | 2014-03-05 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | DCDA | 4 | H | 1988-05-18 | 2015-05-18 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA | Wilkins | DCDA | 6 | H | 1988-06-02 | 2015-06-01 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
DCDA-II | Febco | LF856 | 2.5 | H | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF856 | 2.5 | VU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF856 | 3 | H | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF856 | 3 | VU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF856 | 4 | H | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF856 | 4 | VU | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF856 | 6 | H | 2015-03-13 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF856 | 6 | VU | 2015-03-13 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 2.5 | VUVD | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 2.5 | VUVU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 3 | VUVD | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 3 | VUVU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 4 | VUVD | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 4 | VUVU | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 6 | VUVD | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 6 | VUVU | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),J,K,L,M,N,P,Q
PVB | Ames | A200 | 0.75 | VUH | 1993-04-06 | 2014-04-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
PVB | Ames | A200 | 1 | VUH | 1993-05-25 | 2014-05-25 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
PVB | Ames | A200 | 1.5 | VUH | 1993-06-21 | 2014-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
PVB | Ames | A200 | 2 | VUH | 1993-06-21 | 2014-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
PVB | Apollo/Conbraco | 4050302 | 0.5 | VUH | 1991-09-06 | 2012-09-06 | N | 8 | dd | Y
PVB | Apollo/Conbraco | 4050402 | 0.75 | VUH | 1991-09-06 | 2012-09-06 | N | 8 | (dd) | N
PVB | Apollo/Conbraco | 4050502 | 1 | VUH | 1991-09-06 | 2012-09-06 | N | 8 | (dd) | N
PVB | Apollo/Conbraco | 4050602 | 1.25 | VUH | 1993-12-01 | 2014-12-01 | N | 8 | (dd) | N
PVB | Apollo/Conbraco | 4050702 | 1.5 | VUH | 1993-12-01 | 2014-12-01 | N | 8 | (dd) | N
PVB | Apollo/Conbraco | 4050802 | 2 | VUH | 1993-12-01 | 2014-12-01 | N | 8 | (dd) | N
PVB | Apollo/Conbraco | PVB | 0.5 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 0.75 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 1 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 1.25 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 1.5 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 2 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB4A | 0.5 | VUH | 2010-11-18 | 2013-11-18 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 0.75 | VUH | 2010-11-18 | 2013-11-18 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 1 | VUH | 2010-11-18 | 2013-11-18 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 1.25 | VUH | 2011-04-27 | 2014-04-27 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 1.5 | VUH | 2011-04-27 | 2014-04-27 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 2 | VUH | 2012-01-30 | 2015-01-30 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4V | 0.5 | VUH | 1999-09-23 | 2014-09-23 | N | 9 | (dd) | N |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 0.75 | VUH | 1999-09-23 | 2014-09-23 | N | 9 | (dd) | N |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 1 | VUH | 1999-09-23 | 2014-09-23 | N | 9 | (dd) | N |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 1.25 | VUH | 2002-10-07 | 2014-10-07 | N | 9 | (dd) | N |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 1.5 | VUH | 2002-10-07 | 2014-10-07 | N | 9 | (dd) | N |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 2 | VUH | 2003-06-18 | 2012-06-18 | N | 9 | (dd) | N |  |  | formerly PVB
PVB | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
PVB | Febco | 765 | 0.5 | VUH | 1974-03-26 | 2013-07-01 | N | 5 | (ii),fff,jjj,ooo | N
PVB | Febco | 765 | 0.75 | VUH | 1974-03-26 | 2013-07-01 | N | 5 | (ii),fff,jjj,ooo,xxx | N
PVB | Febco | 765 | 1 | VUH | 1974-03-26 | 2013-07-01 | N | 5 | (ii),fff,jjj,ooo,xxx | N
PVB | Febco | 765 | 1.25 | VUH | 1974-03-26 | 2013-07-01 | N | 5 | (ii),fff,jjj,ooo | N
PVB | Febco | 765 | 1.5 | VUH | 1974-03-26 | 2013-07-01 | N | 5 | (ii),fff,jjj,ooo,xxx | N
PVB | Febco | 765 | 2 | VUH | 1974-03-26 | 2013-07-01 | N | 5 | (ii),fff,ooo,xxx | N
PVB | Febco | 767-FR | 0.5 | VUH | 2006-08-01 | 2012-08-01 | N | 9 | (vv), xx,pppp,rrrrr | N
PVB | Febco | 767-FR | 0.75 | VUH | 2006-08-01 | 2012-08-01 | N | 9 | (vv), xx,pppp,rrrrr | N
PVB | Febco | 767-FR | 1 | VUH | 2006-08-01 | 2012-08-01 | N | 9 | (vv), xx,pppp,rrrrr | N
PVB | Febco | 767-FR | 1.25 | VUH | 2006-08-01 | 2012-08-01 | N | 9 | (vv), xx,pppp,rrrrr | N
PVB | Febco | 767-FR | 1.5 | VUH | 2006-08-01 | 2012-08-01 | N | 9 | (vv), xx,pppp,rrrrr | N
PVB | Febco | 767-FR | 2 | VUH | 2006-08-01 | 2012-08-01 | N | 9 | (vv), xx,pppp,rrrrr | N
PVB | Febco | LF767FR | 0.5 | VUH | 2010-05-04 | 2013-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 0.75 | VUH | 2010-05-04 | 2013-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 1 | VUH | 2010-05-04 | 2013-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 1.25 | VUH | 2010-05-04 | 2013-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 1.5 | VUH | 2010-05-04 | 2013-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 2 | VUH | 2010-05-04 | 2013-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Flomatic | PVB | 0.75 | VUH | 1997-11-21 | 2012-11-21 | N | 9 | (ii) | Y
PVB | Flomatic | PVB | 1 | VUH | 1997-11-21 | 2012-11-21 | N | 9 | (ii) | Y
PVB | Neptune | [5 empty] | N | [5 empty] | See Wilkins
PVB | Watts | 800CMQT | 0.5 | VUH | 1989-07-18 | 2013-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800CMQT | 0.75 | VUH | 1989-07-18 | 2013-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 0.5 | VUH | 1991-07-09 | 2012-07-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 0.75 | VUH | 1991-07-09 | 2012-07-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 1 | VUH | 1991-07-09 | 2012-07-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 1.25 | VUH | 1993-03-25 | 2014-03-25 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 1.5 | VUH | 1993-03-25 | 2014-03-25 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 2 | VUH | 1993-03-25 | 2014-03-25 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M3QT | 0.5 | VUH | 1992-02-24 | 2013-02-24 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M3QT | 0.75 | VUH | 1992-02-24 | 2013-02-24 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M4FR | 0.5 | VUH | 1998-05-12 | 2013-05-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 0.75 | VUH | 1998-05-12 | 2013-05-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 1 | VUH | 1995-09-01 | 2013-09-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 1.25 | VUH | 1997-05-13 | 2015-05-13 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 1.5 | VUH | 1997-05-13 | 2015-05-13 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 2 | VUH | 1997-05-13 | 2015-05-13 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 0.5 | VUH | 1993-09-06 | 2014-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 0.75 | VUH | 1993-04-06 | 2014-04-06 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 1 | VUH | 1993-05-25 | 2014-05-25 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 1.25 | VUH | 1994-05-24 | 2015-05-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 1.5 | VUH | 1993-06-21 | 2014-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 2 | VUH | 1993-06-21 | 2014-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800MQT | 0.5 | VUH | 1989-07-18 | 2013-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800MQT | 0.75 | VUH | 1989-07-18 | 2013-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 0.75 | VUH | 1978-02-14 | 2014-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 1 | VUH | 1978-02-14 | 2014-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 1.25 | VUH | 1978-02-14 | 2014-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 1.5 | VUH | 1978-02-14 | 2014-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 2 | VUH | 1978-02-14 | 2014-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | LF800M4FR | 0.5 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 0.75 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 1 | VUH | 2014-12-05 |  | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 1.25 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 1.5 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 2 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 0.5 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 0.75 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 1 | VUH | 2014-12-05 |  | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 1.25 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 1.5 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 2 | VUH | 2010-01-12 | 2013-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Wilkins | 420 | 0.5 | VUH | 1999-07-17 | 2014-07-17 | N | 9 | (ii),ooo | N
PVB | Wilkins | 420 | 0.75 | VUH | 1999-07-17 | 2014-07-17 | N | 9 | (ii),ooo | N
PVB | Wilkins | 420 | 1 | VUH | 2000-09-29 | 2012-09-29 | N | 9 | (ii),ooo | N
PVB | Wilkins | 420XL | 0.5 | VUH | 2011-03-21 | 2014-03-21 | Y | 9 | (iiii) | N
PVB | Wilkins | 420XL | 0.75 | VUH | 2011-03-21 | 2014-03-21 | Y | 9 | (iiii) | N
PVB | Wilkins | 420XL | 1 | VUH | 2011-08-03 | 2014-08-03 | Y | 9 | (iiii) | Y
PVB | Wilkins | 720A | 0.5 | VUH | 1978-08-28 | 2014-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
PVB | Wilkins | 720A | 0.75 | VUH | 1978-08-28 | 2014-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
PVB | Wilkins | 720A | 1 | VUH | 1978-08-28 | 2014-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
PVB | Wilkins | 720A | 1.25 | VUH | 1978-08-28 | 2014-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
PVB | Wilkins | 720A | 1.5 | VUH | 1978-08-28 | 2014-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
PVB | Wilkins | 720A | 2 | VUH | 1978-08-28 | 2014-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
RP | Ames | 4000B | 0.5 | H | 1996-09-10 | 2014-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously Approved 8th Ed. (26 May 1993)
RP | Ames | 4000B | 0.75 | H | 1992-10-31 | 2013-10-31 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 1.25 | H | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 1.5 | H | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 2 | H | 1996-09-10 | 2014-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B-FP | 0.75 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Ames | 4000B-FP | 1 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Ames | 4000B-FP | 1.25 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Ames | 4000B-FP | 1.5 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Ames | 4000B-FP | 2 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Ames | 4000BM2 | 1 | H | 1998-05-18 | 2013-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000BM2-FP | 1 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Ames | 4000BM3 | 0.75 | H | 2000-03-27 | 2015-03-27 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000BM3-FP | 0.75 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Ames | 4000CIV | 2.5 | H | 2000-07-07 | 2012-07-07 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu | N
RP | Ames | 4000CIV | 3 | H | 2000-07-07 | 2012-07-07 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu | N
RP | Ames | 4000CIV | 4 | H | 2000-06-19 | 2012-06-19 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
RP | Ames | 4000CIV | 6 | H | 2000-06-19 | 2012-06-19 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | N
RP | Ames | 4000CIV | 8 | H | 2000-06-19 | 2012-06-19 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu | N
RP | Ames | 4000CIV | 10 | H | 2000-06-19 | 2012-06-19 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu | N
RP | Ames | 4000RP | 4 | H | 1987-10-13 | 2014-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N |  |  | formerly Model RP
RP | Ames | 4000RP | 6 | H | 1987-10-13 | 2014-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N |  |  | formerly Model RP
RP | Ames | 4000RP | 8 | H | 1987-10-13 | 2014-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N |  |  | formerly Model RP
RP | Ames | 4000RP | 10 | H | 1987-10-13 | 2014-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N |  |  | formerly Model RP
RP | Ames | 4000SS | 2.5 | H | 1994-04-15 | 2015-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 2.5 | H | 1994-04-15 | 2015-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 4000SS | 3 | H | 1994-04-15 | 2015-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 3 | H | 1994-04-15 | 2015-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 4000SS | 4 | H | 1994-04-15 | 2015-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 4 | H | 1994-04-15 | 2015-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 4000SS | 6 | H | 1997-09-22 | 2012-09-22 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 6 | H | 1997-09-22 | 2012-09-22 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 400B | 0.75 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 0.75 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 1 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 1 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 1.25 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 1.25 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 1.5 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 1.5 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 2 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B | 2 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-A | 0.75 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-A | 1 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-A | 1.25 | VUVD | 2006-09-05 | 2012-09-05 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-A | 1.5 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-A | 2 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-Z | 0.75 | VUVU | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-Z | 1 | VUVU | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-Z | 1.25 | VUVU | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-Z | 1.5 | VUVU | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 400B-Z | 2 | VUVU | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | Colt 400 | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 2.5 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 3 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 4 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 4 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 6 | H | 2004-09-29 | 2013-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Colt 400 | 6 | H | 2004-09-29 | 2013-09-29 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Colt 400 | 8 | H | 2007-08-13 | 2013-08-13 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Colt 400 | 8 | H | 2007-08-13 | 2013-08-13 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Colt 400 | 10 | H | 2009-07-22 | 2012-07-22 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb,nnnnn | N
RP | Ames | Colt 400 | 10 | H | 2009-07-22 | 2012-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Colt 400BF | 4 | H | 2007-09-17 | 2013-09-17 | Y | 9 | (yyy) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400BF | 6 | H | 2007-09-17 | 2013-09-17 | Y | 9 | (yyy) | N
RP | Ames | Colt 400N | 2.5 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 2.5 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 3 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 3 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 4 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 4 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 6 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Ames | Colt 400N | 6 | VUVD | 2010-11-15 | 2013-11-15 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Ames | Colt 400N | 8 | VUVD | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | Colt 400Z | 2.5 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 2.5 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 3 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 3 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 4 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 4 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 8 | VUVU | 2013-06-14 |  | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Ames | Colt 400Z | 8 | VUVU | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | LF4000B | 0.5 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
RP | Ames | LF4000BM2 | 1 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
RP | Ames | LF4000BM2 | 1.25 | H | 2013-09-25 |  | Y | 8 | (hhhh) | N
RP | Ames | LF4000BM2 | 1.5 | H | 2013-09-25 |  | Y | 8 | (hhhh) | N
RP | Ames | LF4000BM2 | 2 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
RP | Ames | LF4000BM3 | 0.75 | H | 2013-09-25 |  | Y | 9 | (hhhh) | N
RP | Ames | Maxim 400 | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 2.5 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 3 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 4 | H | 2005-01-18 | 2014-01-18 | N | 9 | (ppp),qqq,aaa,bbbb,nnnnn | N
RP | Ames | Maxim 400 | 4 | H | 2005-01-18 | 2014-01-18 | Y | 9 | kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400 | 6 | H | 2007-08-13 | 2013-08-13 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400 | 6 | H | 2007-08-13 | 2013-08-13 | Y | 9 | cccc,dddd,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400 | 8 | H | 2009-07-22 | 2012-07-22 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400 | 8 | H | 2009-07-22 | 2012-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400 | 10 | H | 2009-07-22 | 2012-07-22 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb | N
RP | Ames | Maxim 400 | 10 | H | 2009-07-22 | 2012-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 2.5 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400N | 2.5 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 3 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400N | 3 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 4 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Ames | Maxim 400N | 4 | VUVD | 2010-11-15 | 2013-11-15 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Ames | Maxim 400N | 6 | VUVD | 2013-06-14 |  | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Ames | Maxim 400N | 6 | VUVD | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | Maxim 400Z | 2.5 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400Z | 2.5 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400Z | 3 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400Z | 3 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400Z | 6 | VUVU | 2013-06-14 |  | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Ames | Maxim 400Z | 6 | VUVU | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | RP | 4 | [9 empty] | model designation changed to 4000RP
RP | Ames | RP | 6 | [9 empty] | model designation changed to 4000RP
RP | Ames | RP | 8 | [9 empty] | model designation changed to 4000RP
RP | Ames | RP | 10 | [9 empty] | model designation changed to 4000RP
RP | Ames | U400B | 1 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B | 1 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B | 1.25 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B | 1.25 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B | 1.5 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B | 1.5 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B | 2 | H | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B | 2 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B-A | 0.75 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B-A | 1 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B-A | 1.25 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B-A | 1.5 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Ames | U400B-A | 2 | VUVD | 2006-06-20 | 2012-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Apollo/Conbraco | 2020499T | 0.75 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020002 | 3 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020003 | 3 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020005 | 3 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020102 | 0.25 | H | 1991-05-03 | 2015-05-03 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020199T | 0.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40201A2 | 0.25 | H | 1996-04-19 | 2014-04-19 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40201A2S | 0.25 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40201T2 | 0.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40201T2S | 0.25 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 4020202 | 0.375 | H | 1991-05-03 | 2015-05-03 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020299T | 0.375 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40202A2 | 0.375 | H | 1996-04-19 | 2014-04-19 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40202A2S | 0.375 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40202T2 | 0.375 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40202T2S | 0.375 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 4020302 | 0.5 | H | 1991-05-03 | 2014-05-03 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020399T | 0.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40203A2 | 0.5 | H | 1996-04-19 | 2014-04-19 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40203A2S | 0.5 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40203T2 | 0.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40203T2S | 0.5 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 4020402 | 0.75 | H | 1989-05-08 | 2013-05-08 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40204A2 | 0.75 | H | 1991-11-27 | 2012-11-27 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40204A2S | 0.75 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40204A2U | 0.75 | [9 empty] | model designation changed to RP40N
RP | Apollo/Conbraco | 40204A2Z | 0.75 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40204T2 | 0.75 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40204TC2 | 0.75 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40204TCU | 0.75 | VUVD | 1998-11-30 | 2013-11-22 | N | 8 | (dd) | N
RP | Apollo/Conbraco | 4020502 | 1 | H | 1989-05-08 | 2013-05-08 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020599T | 1 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40205A2 | 1 | H | 1991-11-27 | 2012-11-27 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40205A2S | 1 | [9 empty] | model designation changed to 40205T2S
RP | Apollo/Conbraco | 40205A2U | 1 | [9 empty] | model designation changed to 40205T2U
RP | Apollo/Conbraco | 40205A2Z | 1 | [9 empty] | model designation changed to 40205T2Z
RP | Apollo/Conbraco | 40205T2 | 1 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40205T2S | 1 | H | 1994-08-16 | 2012-08-16 | N | 8 | (uuu) | N |  |  | formerly 40205A2S
RP | Apollo/Conbraco | 40205T2U | 1 | VUVD | 1993-09-15 | 2014-09-15 | N | 8 | (dd) | N |  |  | formerly 40205A2U
RP | Apollo/Conbraco | 40205T2Z | 1 | VUVU | 1993-09-15 | 2014-09-15 | N | 8 | (dd) | N |  |  | formerly 40205A2Z
RP | Apollo/Conbraco | 40205TC2 | 1 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40205TCU | 1 | VUVD | 1998-11-30 | 2013-11-22 | N | 8 | (dd) | N
RP | Apollo/Conbraco | 4020602 | 1.25 | H | 1992-04-06 | 2013-04-06 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020699T | 1.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40206A2 | 1.25 | H | 1993-06-21 | 2014-06-21 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40206A2U | 1.25 | [9 empty] | model designation changed to RP40N
RP | Apollo/Conbraco | 40206A2Z | 1.25 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40206T2 | 1.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40206T2U | 1.25 | [9 empty] | model designation changed to RP40N
RP | Apollo/Conbraco | 40206T2Z | 1.25 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 4020702 | 1.5 | H | 1989-03-17 | 2013-03-17 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020799T | 1.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40207A2 | 1.5 | H | 1992-09-16 | 2013-09-16 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40207A2U | 1.5 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40207A2Z | 1.5 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40207T2 | 1.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40207T2U | 1.5 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40207T2Z | 1.5 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 4020802 | 2 | H | 1989-03-17 | 2013-03-17 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020899T | 2 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40208A2 | 2 | H | 1992-09-16 | 2013-09-16 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40208A2U | 2 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40208A4 | 2 | H | 2000-05-24 | 2015-05-24 | N | 8 | rrr | Y
RP | Apollo/Conbraco | 40208AZ2 | 2 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40208T2 | 2 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40208T2U | 2 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40208T2Z | 2 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 4020902 | 2.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020903 | 2.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020905 | 2.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020A02 | 4 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020A03 | 4 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020A05 | 4 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020C02 | 6 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020C03 | 6 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020C05 | 6 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020E02 | 8 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020E03 | 8 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020G02 | 10 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020G03 | 10 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4D-200 | 2.5 | H | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200 | 3 | H | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200 | 4 | H | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200U | 2.5 | VUVD | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200U | 3 | VUVD | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200U | 4 | VUVD | 2009-03-11 | 2015-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | RP40 | 0.25 | H | 1998-09-16 | 2013-09-16 | N | 8 | (dd) | N |  |  | formerly 4020199T, 40201T2
RP | Apollo/Conbraco | RP40 | 0.375 | H | 1998-09-16 | 2013-09-16 | N | 8 | (dd) | N |  |  | formerly 4020299T, 40202T2
RP | Apollo/Conbraco | RP40 | 0.5 | H | 1994-09-15 | 2013-09-15 | N | 8 | (dd) | N |  |  | formerly 4020399T, 40203T2
RP | Apollo/Conbraco | RP40 | 0.75 | H | 1998-09-16 | 2013-09-16 | N | 8 | (dd) | N |  |  | formerly 2020499T, 40204T2, 40204TC2
RP | Apollo/Conbraco | RP40 | 1 | H | 1998-09-16 | 2013-09-16 | N | 8 | (dd) | N |  |  | formerly 4020599T, 40205T2, 40205TC2
RP | Apollo/Conbraco | RP40 | 1.25 | H | 1998-09-16 | 2013-09-16 | N | 8 | (dd) | N |  |  | formerly 4020699T, 40206T2
RP | Apollo/Conbraco | RP40 | 1.5 | H | 1998-09-16 | 2013-09-16 | N | 8 | (dd) | N |  |  | formerly 4020799T, 40207T2
RP | Apollo/Conbraco | RP40 | 2 | H | 1998-09-16 | 2013-09-16 | N | 8 | (dd) | N |  |  | formerly 4020899T, 40208T2
RP | Apollo/Conbraco | RP40 | 2.5 | H | 1991-04-08 | 2015-04-08 | N | 8 | (tt),bb,cc,ee,ll,mm,uu,mmm | N |  |  | formerly 4020902, 4020903, 4020905
RP | Apollo/Conbraco | RP40 | 3 | H | 1991-04-08 | 2015-04-08 | N | 8 | (tt),bb,cc,ee,ll,mm,uu,mmm | N |  |  | formerly 4020002, 4020003, 4020005
RP | Apollo/Conbraco | RP40 | 4 | H | 1991-04-08 | 2015-04-08 | N | 8 | (tt),bb,cc,ee.ll,mm,uu,mmm | N |  |  | formerly 4020A02, 4020A03, 4020A05
RP | Apollo/Conbraco | RP40 | 6 | H | 1991-04-08 | 2015-04-08 | N | 8 | (tt),bb,ee,ll | N |  |  | formerly 4020C02, 4020C03, 4020C05
RP | Apollo/Conbraco | RP40 | 8 | H | 1991-10-22 | 2012-10-22 | N | 8 | (tt),bb,cc,ee,ll,mm,uu | N |  |  | formerly 4020E02, 4020E03
RP | Apollo/Conbraco | RP40 | 10 | H | 1993-04-13 | 2014-04-13 | N | 8 | (tt),bb,cc,ee,ll,mm,uu | N |  |  | formerly 4020G02, 4020G03
RP | Apollo/Conbraco | RP40N | 0.75 | VUVD | 1992-11-06 | 2013-11-06 | N | 8 | (dd) | N |  |  | formerly 40204A2U
RP | Apollo/Conbraco | RP40N | 1.25 | VUVD | 1995-02-02 | 2013-02-02 | N | 8 | (dd) | N |  |  | formerly 40206A2U, 40206T2U
RP | Apollo/Conbraco | RP40U | 1.5 | VUVD | 1995-02-02 | 2013-02-02 | N | 8 | (dd) | N |  |  | formerly 40207A2U, 40207T2U
RP | Apollo/Conbraco | RP40U | 2 | VUVD | 1995-02-02 | 2013-02-02 | N | 8 | (dd) | N |  |  | formerly 40208A2U, 40208T2U
RP | Apollo/Conbraco | RP40Z | 0.75 | VUVU | 1992-11-06 | 2013-11-06 | N | 8 | (dd) | N |  |  | formerly 40204A2Z
RP | Apollo/Conbraco | RP40Z | 1.25 | VUVU | 1995-02-02 | 2013-02-02 | N | 8 | (dd) | N |  |  | formerly 40206A2Z, 40206T2Z
RP | Apollo/Conbraco | RP40Z | 1.5 | VUVU | 1995-02-02 | 2013-02-02 | N | 8 | (dd) | N |  |  | formerly 40207A2Z, 40207T2Z
RP | Apollo/Conbraco | RP40Z | 2 | VUVU | 1995-02-02 | 2013-02-02 | N | 8 | (dd) | N |  |  | formerly 40208AZ2, 40208T2Z
RP | Apollo/Conbraco | RP4A | 0.5 | H | 2011-11-29 | 2014-10-29 | N | 9 | (iiiii),sssss | N
RP | Apollo/Conbraco | RP4A | 0.75 | H | 2011-06-14 | 2014-06-14 | N | 9 | (iiiii),sssss,wwww | N
RP | Apollo/Conbraco | RP4A | 1 | H | 2011-09-27 | 2014-09-27 | N | 9 | (iiiii),sssss,wwww | N
RP | Apollo/Conbraco | RP4A | 1.25 | H | 2013-12-11 |  | N | 9 | (iiiii),sssss,wwww | N
RP | Apollo/Conbraco | RP4A | 1.5 | H | 2013-12-11 |  | N | 9 | (iiiii),sssss,wwww | N
RP | Apollo/Conbraco | RP4A | 2 | H | 2011-11-29 | 2014-10-29 | N | 9 | (iiiii),sssss,wwww | N
RP | Apollo/Conbraco | RPLF40 | 0.5 | H | 2010-11-18 | 2013-11-18 | Y | 9 | (jjjjj) | N
RP | Apollo/Conbraco | RPLF40 | 1.25 | H | 2010-11-18 | 2013-11-18 | Y | 9 | (jjjjj) | N
RP | Apollo/Conbraco | RPLF40 | 1.5 | H | 2010-11-18 | 2013-11-18 | Y | 9 | (jjjjj) | N
RP | Apollo/Conbraco | RPLF40 | 2 | H | 2010-11-18 | 2013-11-18 | Y | 9 | (jjjjj) | N
RP | Apollo/Conbraco | RPLF4A | 0.5 | H | 2011-11-29 | 2014-10-29 | Y | 9 | (jjjjj),ttttt,uuuuu | N
RP | Apollo/Conbraco | RPLF4A | 0.75 | H | 2011-06-14 | 2014-06-14 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 1 | H | 2011-09-27 | 2014-09-27 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 1.25 | H | 2013-12-11 |  | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 1.5 | H | 2013-12-11 |  | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 2 | H | 2011-11-29 | 2014-10-29 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 2.5 | H | 2014-02-25 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4A | 3 | H | 2014-02-25 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4A | 4 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4A | 6 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4AN | 2.5 | VUVD | 2015-04-27 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4AN | 2.5 | VUVU | 2015-04-27 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4AN | 3 | VUVD | 2015-04-27 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4AN | 3 | VUVU | 2015-04-27 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4AN | 4 | VUVD | 2014-05-15 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPS40 | 0.25 | H | 1996-04-19 | 2014-04-19 | N | 8 | (uuu) | N |  |  | formerly 40201A2S, 40201T2S
RP | Apollo/Conbraco | RPS40 | 0.375 | H | 1996-04-19 | 2014-04-19 | N | 8 | (uuu) | N |  |  | formerly 40202A2S, 40202T2S
RP | Apollo/Conbraco | RPS40 | 0.5 | H | 1996-04-19 | 2014-04-19 | N | 8 | (dd) | N |  |  | formerly 40203A2S, 40203T2S
RP | Apollo/Conbraco | RPS40 | 0.75 | H | 1994-08-16 | 2012-08-16 | N | 8 | (uuu) | N |  |  | formerly 40204A2S
RP | ARI | RP 500 | 0.5 | H | 2013-01-03 |  | N | 9 | (ooooo), ii, ooo | N
RP | ARI | RP 500 | 0.5 | H | 2014-02-18 |  | Y | 9 | (ooooo) | N
RP | ARI | RP 500 | 0.75 | H | 2007-03-02 | 2013-03-02 | N | 9 | (ii),ooo, ooooo | N
RP | ARI | RP 500 | 0.75 | H | 2014-02-18 |  | Y | 9 | (ooooo) | N
RP | ARI | RP 500 | 1 | H | 2007-03-02 | 2013-03-02 | N | 9 | (ii),ooo, ooooo | N
RP | ARI | RP 500 | 1 | H | 2014-02-18 |  | Y | 9 | (ooooo) | N
RP | ARI | RP 500 | 1.25 | H | 2014-02-18 |  | Y | 10 | (ooooo) | N
RP | ARI | RP 500 | 1.5 | H | 2014-02-18 |  | Y | 10 | (ooooo) | N
RP | ARI | RP 500 | 2 | H | 2014-02-18 |  | Y | 10 | (ooooo) | N
RP | Cash Acme | RP 500 | 0.75 | H | 2012-04-19 | 2015-04-19 | Y | 9 | (ii),ooo | N
RP | Cash Acme | RP 500 | 1 | H | 2012-04-19 | 2015-04-19 | Y | 9 | (ii),ooo | N
RP | Cash Acme | RP100 | 0.75 | H | 2009-04-07 | 2015-04-07 | N | 8 | (ii) | N
RP | Cash Acme | RP100 | 1 | H | 2009-04-07 | 2015-04-07 | N | 8 | (ii) | N
RP | Cash Acme | RP100 | 1.5 | H | 2009-04-07 | 2015-04-07 | N | 8 | (ii) | N
RP | Cash Acme | RP100 | 2 | H | 2009-04-07 | 2015-04-07 | N | 8 | (ii) | N
RP | Cash Acme | RP200 | 0.5 | H | 2009-04-07 | 2015-04-07 | N | 8 | (ii) | N
RP | Cash Acme | RP200 | 0.75 | H | 2009-04-07 | 2015-04-07 | N | 8 | (ii) | N
RP | Cla-Val | RP4 | 8 | H | 1989-06-22 | 2013-06-22 | N | 8 | (gg),hh,qq,rr | Y
RP | Cla-Val | RP4 | 10 | H | 1989-06-22 | 2013-06-22 | N | 8 | (gg),hh,qq,rr | Y
RP | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
RP | Febco | 860 | 0.5 | H | 1998-04-09 | 2013-04-09 | N | 9 | (fff),ooo | N
RP | Febco | 860 | 0.75 | H | 1997-11-21 | 2012-11-21 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 1 | H | 1997-11-21 | 2012-11-21 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 1.25 | H | 1998-06-04 | 2013-06-04 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 1.5 | H | 1998-04-09 | 2013-04-09 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 2 | H | 1998-04-09 | 2013-04-09 | N | 9 | (fff),ooo | N
RP | Febco | 860 | 2.5 | H | 1996-04-19 | 2014-04-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu.zzz,cccc,ffff,gggg | N
RP | Febco | 860 | 3 | H | 1996-04-19 | 2014-04-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu.zzz,cccc,ffff,gggg | N
RP | Febco | 860 | 4 | H | 1995-05-31 | 2013-05-31 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 860 | 6 | H | 1995-08-07 | 2013-08-07 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 860 | 8 | H | 1995-10-04 | 2013-10-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 867 | 2.5 | H | 2006-08-01 | 2012-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | N
RP | Febco | 867 | 3 | H | 2006-08-01 | 2012-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, eee, fff | N
RP | Febco | 880 | 2.5 | VUVD | 1995-05-24 | 2013-05-24 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 3 | VUVD | 1995-05-24 | 2013-05-24 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 4 | VUVD | 1995-03-10 | 2013-03-10 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 6 | VUVD | 1995-05-19 | 2013-05-19 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 8 | VUVD | 1995-05-19 | 2013-05-19 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 10 | VUVD | 1996-10-04 | 2014-10-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 760 | 2.5 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760 | 2.5 | H | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760 | 3 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760 | 3 | H | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760 | 4 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760 | 4 | H | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760 | 6 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760 | 6 | H | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760 | 8 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb | N
RP | Febco | 760 | 8 | H | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760 | 10 | H | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb | N
RP | Febco | 760 | 10 | H | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760N | 2.5 | VUVD | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760N | 2.5 | VUVD | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760N | 3 | VUVD | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760N | 3 | VUVD | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760N | 4 | VUVD | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760N | 4 | VUVD | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760Z | 2.5 | VUVU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760Z | 2.5 | VUVU | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760Z | 3 | VUVU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760Z | 3 | VUVU | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 760Z | 4 | VUVU | 2009-09-17 | 2012-09-17 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Febco | 760Z | 4 | VUVU | 2009-09-17 | 2012-09-17 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Febco | 825Y | 0.75 | H | 1982-03-19 | 2015-03-19 | N | 6 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825Y | 1 | H | 1982-03-19 | 2015-03-19 | N | 6 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825Y | 1.25 | H | 1982-06-03 | 2015-06-01 | N | 6 | ii,fff,jjj,ooo | Y
RP | Febco | 825Y | 1.5 | H | 1982-08-06 | 2012-08-06 | N | 6 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825Y | 2 | H | 1982-08-06 | 2012-08-06 | N | 6 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | H | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | HVD | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | VUH | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | VUVD | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | H | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | HVD | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | VUH | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | VUVD | 1990-03-05 | 2014-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | H | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | HVD | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | VUH | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | VUVD | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | H | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | HVD | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | VUH | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | VUVD | 1989-05-08 | 2013-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YAR | 0.75 | H | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 0.75 | HVD | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 0.75 | VUH | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 0.75 | VUVD | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | H | 1993-01-21 | 2014-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | HVD | 1993-01-21 | 2014-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | VUH | 1993-01-21 | 2014-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | VUVD | 1993-01-21 | 2014-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | H | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | HVD | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | VUH | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | VUVD | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 2 | H | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YAR | 2 | HVD | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YAR | 2 | VUH | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YAR | 2 | VUVD | 1993-08-19 | 2014-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YD | 2.5 | H | 1989-02-24 | 2013-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N
RP | Febco | 825YD | 3 | H | 1989-02-24 | 2013-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N
RP | Febco | 825YD | 4 | H | 1989-02-24 | 2013-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N
RP | Febco | 825YD | 6 | H | 1989-02-24 | 2013-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N
RP | Febco | 825YD | 8 | H | 1989-02-24 | 2013-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N
RP | Febco | 825YD | 10 | H | 1989-02-24 | 2013-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | N
RP | Febco | 825YR | 0.75 | H | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj | Y
RP | Febco | 825YR | 1 | H | 1993-01-22 | 2014-01-22 | N | 8 | ii,fff,jjj | Y
RP | Febco | 825YR | 1.5 | H | 1993-07-23 | 2014-07-23 | N | 8 | ii,fff,jjj | Y
RP | Febco | 825YR | 2 | H | 1993-07-23 | 2014-07-23 | N | 8 | ii,fff | Y
RP | Febco | 860U | 0.5 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 0.75 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 1 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 1.25 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 1.5 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 2 | H | 1998-10-12 | 2013-10-12 | N | 9 | (kkk) | N
RP | Febco | 880V | 2.5 | VUVD | 1995-06-30 | 2013-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 2.5 | VUVU | 1995-06-30 | 2013-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 3 | VUVD | 1995-06-30 | 2013-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 3 | VUVU | 1995-06-30 | 2013-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 4 | VUVD | 1995-08-08 | 2013-08-08 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 4 | VUVU | 1995-08-08 | 2013-08-08 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 6 | VUVD | 1995-07-05 | 2013-07-05 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 6 | VUVU | 1995-07-05 | 2013-07-05 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 8 | VUVD | 1996-12-18 | 2014-12-18 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 8 | VUVU | 1996-12-18 | 2014-12-18 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 10 | VUVD | 1997-06-17 | 2012-06-17 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | 880V | 10 | VUVU | 1997-06-17 | 2012-06-17 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | N
RP | Febco | LF825Y | 0.75 | H | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825Y | 1 | H | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825Y | 1.5 | H | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825Y | 2 | H | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 0.75 | H | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 0.75 | HVD | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 0.75 | VUH | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 0.75 | VUVD | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1 | H | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1 | HVD | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1 | VUH | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1 | VUVD | 2010-02-18 | 2013-02-18 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1.5 | H | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1.5 | HVD | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1.5 | VUH | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 1.5 | VUVD | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 2 | H | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 2 | HVD | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 2 | VUH | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF825YA | 2 | VUVD | 2010-03-25 | 2013-03-25 | Y | 8 | (hhhh) | N
RP | Febco | LF860 | 0.5 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 0.75 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 1 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 1.25 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 1.5 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 2 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 2.5 | H | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF860 | 3 | H | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF860 | 4 | H | 2013-06-14 |  | Y | 9 | (ll), mm | N
RP | Febco | LF860 | 6 | H | 2013-06-14 |  | Y | 9 | (ll), mm | N
RP | Febco | LF860 | 8 | H | 2013-09-03 |  | Y | 9 | (ll), mm | N
RP | Febco | LF860 | 10 | H | 2013-09-25 |  | Y | 9 | (ll), mm | N
RP | Febco | LF860U | 0.5 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 0.75 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 1 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 1.25 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 1.5 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 2 | H | 2013-09-03 |  | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF880V | 2.5 | VUVD | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 2.5 | VUVU | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 3 | VUVD | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 3 | VUVU | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 4 | VUVD | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 4 | VUVU | 2013-05-28 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 6 | VUVD | 2013-09-03 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 6 | VUVU | 2013-09-03 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 8 | VUVD | 2013-11-26 |  | Y | 9 | (ll), mm | N
RP | Febco | LF880V | 8 | VUVU | 2013-11-26 |  | Y | 9 | (ll), mm | N
RP | Flomatic | RPZ | 0.75 | H | 1994-06-07 | 2012-06-17 | N | 8 | ii | Y
RP | Flomatic | RPZ | 1 | H | 1994-06-07 | 2012-06-17 | N | 8 | ii | Y
RP | Flomatic | RPZ | 1.5 | H | 1995-05-10 | 2013-05-10 | N | 8 | ii | Y
RP | Flomatic | RPZ | 2 | H | 1995-05-10 | 2013-05-10 | N | 8 | ii | Y
RP | Flomatic | RPZ | 2.5 | H | 1997-02-14 | 2015-02-14 | N | 8 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd | Y
RP | Flomatic | RPZ | 3 | H | 1997-02-14 | 2015-02-14 | N | 8 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd | Y
RP | Flomatic | RPZ | 4 | H | 1999-01-28 | 2013-01-28 | N | 9 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd | Y
RP | Flomatic | RPZ | 4 | H | 1999-01-28 | 2013-01-28 | Y | 9 | ddddd | Y
RP | Flomatic | RPZ | 6 | H | 2002-01-31 | 2014-01-31 | N | 9 | (gg),hh,jj,kk,ll,mm,yy,zz,ccc,ddd | Y
RP | Flomatic | RPZ | 6 | H | 2002-01-31 | 2014-01-31 | Y | 9 | ddddd | Y
RP | Flomatic | RPZ | 8 | H | 2005-02-05 | 2014-02-05 | N | 9 | (gg), hh, jj, kk, ll, mm, yy, zz, ccc, ddd | Y
RP | Flomatic | RPZE | 0.75 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
RP | Flomatic | RPZE | 1 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
RP | Flomatic | RPZE | 1.5 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
RP | Flomatic | RPZE | 2 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y
RP | Flomatic | RPZE II | 0.5 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y |  |  | formerly RPZIIE
RP | Flomatic | RPZE II | 0.75 | H | 2001-06-07 | 2013-06-07 | Y | 8 | (hhhhh) | Y |  |  | formerly RPZIIE
RP | Flomatic | RPZII | 0.5 | H | 1997-08-15 | 2012-08-15 | N | 8 | ii | Y
RP | Flomatic | RPZII | 0.75 | H | 1997-08-15 | 2012-08-15 | N | 8 | ii | Y
RP | Flomatic | RPZIIE | 0.5 | [9 empty] | model designation changed to RPZE II
RP | Flomatic | RPZIIE | 0.75 | [9 empty] | model designation changed to RPZE II
RP | Neptune | [5 empty] | N | [5 empty] | See Wilkins
RP | Watts | 957 | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 2.5 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 3 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 4 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 4 | H | 2002-10-07 | 2014-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 6 | H | 2004-12-20 | 2013-12-20 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Watts | 957 | 6 | H | 2004-12-20 | 2013-12-20 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 957 | 8 | H | 2007-08-13 | 2013-08-13 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Watts | 957 | 8 | H | 2007-08-13 | 2013-08-13 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 957 | 10 | H | 2009-07-22 | 2012-07-22 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Watts | 957 | 10 | H | 2009-07-22 | 2012-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 2.5 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 3 | H | 2002-10-07 | 2014-10-07 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 4 | H | 2005-01-18 | 2014-01-18 | N | 9 | (ppp),qqq,aaaa,bbbb,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 6 | H | 2007-08-13 | 2013-08-13 | N | 9 | (ppp),qqq,sss, ttt, aaaa,bbbb,cccc,dddd,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 8 | H | 2009-07-22 | 2012-07-22 | N | 9 | (ppp),qqq,sss,ttt,zzz,aaaa,bbbb,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 10 | H | 2009-07-22 | 2012-07-22 | N | 9 | (ppp),qqq,sss,ttt,zzz,aaaa,bbbb,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Watts | 994 | 2.5 | H | 1994-04-15 | 2015-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 2.5 | H | 1994-04-15 | 2015-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 994 | 3 | H | 1994-04-15 | 2015-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 3 | H | 1994-04-15 | 2015-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 994 | 4 | H | 1994-04-15 | 2015-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 4 | H | 1994-04-15 | 2015-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 994 | 6 | H | 1997-09-22 | 2012-09-22 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 6 | H | 1997-09-22 | 2012-09-22 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 009 | 2.5 | H | 1990-08-31 | 2014-08-31 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | N
RP | Watts | 009 | 3 | H | 1990-08-31 | 2014-08-31 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,eee,ffff,gggg | N
RP | Watts | 009M1PCQT | 1.25 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1QT | 1.25 | H | 1992-06-30 | 2013-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1QT | 1.5 | H | 1992-06-30 | 2013-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1QT | 2 | H | 1991-12-19 | 2012-12-19 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M2-FP | 1 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2-FP | 1.25 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2-FP | 1.5 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2-FP | 2 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2PCQT | 0.75 | H | 2002-10-07 | 2014-10-07 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 1 | H | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 1.25 | H | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 1.5 | H | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 2 | H | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 0.75 | H | 1992-10-31 | 2013-10-31 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 1 | H | 1998-05-18 | 2013-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 1.25 | H | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 1.5 | H | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 2 | H | 1996-09-10 | 2014-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M3-FP | 0.75 | H | 2009-09-01 | 2012-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M3QT | 0.75 | H | 1999-10-18 | 2014-10-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009PCQT | 0.5 | H | 1995-02-17 | 2013-02-17 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009PCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009PCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 1.25 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 0.25 | H | 1995-08-07 | 2013-08-07 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | 009QT | 0.375 | H | 1995-08-07 | 2013-08-07 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | 009QT | 0.5 | H | 1996-09-10 | 2014-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously approved 8th Ed. 26 May 1993
RP | Watts | 009QT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009QT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 1.25 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 1.5 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 2 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009SSM1PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSM1QT | 2 | H | 1991-12-19 | 2012-12-19 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 1.25 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 1.25 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 1.5 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 2 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | 909 | 2.5 | H | 1986-06-12 | 2013-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,ffff,gggg | N
RP | Watts | 909 | 3 | H | 1986-06-12 | 2013-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 4 | H | 1982-01-15 | 2015-01-15 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 6 | H | 1981-07-06 | 2014-07-06 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | N |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 8 | H | 1981-07-06 | 2014-07-06 | N | 6 |  | Y |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 10 | H | 1981-07-06 | 2014-07-06 | N | 6 |  | Y |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909BB | 2.5 | H | 1983-02-04 | 2013-02-04 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | N
RP | Watts | 909BB | 3 | H | 1983-02-04 | 2013-02-04 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | N
RP | Watts | 909HWQT | 0.75 | H | 1979-09-29 | 2012-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 909HWQT | 1 | H | 1979-09-29 | 2012-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 909HWQT | 1.25 | [9 empty] | model designation changed to 909M1HWQT
RP | Watts | 909HWQT | 1.5 | [9 empty] | model designation changed to 909M1HWQT
RP | Watts | 909HWQT | 2 | [9 empty] | model designation changed to 909M1HWQT
RP | Watts | 909M1 | 8 | H | 1989-05-01 | 2013-05-01 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ww,ffff,gggg | N
RP | Watts | 909M1 | 10 | H | 1989-05-01 | 2013-05-01 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,ffff,gggg | N
RP | Watts | 909M1HWQT | 1.25 | H | 1980-02-07 | 2013-02-07 | N | 5 | (vv),xx,ooo,hhhh,rrrrr | N |  |  | formerly 909HWQT
RP | Watts | 909M1HWQT | 1.5 | H | 1980-02-07 | 2013-02-07 | N | 5 | (vv),xx,ooo,hhhh,rrrrr | N |  |  | formerly 909HWQT
RP | Watts | 909M1HWQT | 2 | H | 1980-02-07 | 2013-02-07 | N | 5 | (vv),xx,ooo,hhhh,rrrrr | N |  |  | formerly 909HWQT
RP | Watts | 909M1PCHWQT | 1.25 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,rrrrr | N
RP | Watts | 909M1PCHWQT | 1.5 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,rrrrr | N
RP | Watts | 909M1PCHWQT | 2 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,rrrrr | N
RP | Watts | 909M1QT | 1.25 | H | 1982-01-15 | 2015-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | formerly 909QT
RP | Watts | 909M1QT | 1.5 | H | 1982-01-15 | 2015-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | formerly 909QT
RP | Watts | 909M1QT | 2 | H | 1982-01-15 | 2015-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | formerly 909QT
RP | Watts | 909NRS | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909PCHWQT | 0.75 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 909PCHWQT | 1 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 909PCM1QT | 1.25 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 909PCM1QT | 1.5 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 909PCM1QT | 2 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 909PCQT | 0.75 | H | 1998-10-09 | 2013-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously Approved 8th Ed (2 February 1995) 9th Ed. for Ser. Nos. 464100 and higher
RP | Watts | 909PCQT | 0.75 | VU | 1998-10-09 | 2013-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Serial number 464100 and higher
RP | Watts | 909PCQT | 1 | H | 1998-10-09 | 2013-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously Approved 8th Ed (2 February 1995) 9th Ed. for Ser. Nos. 464100 and higher
RP | Watts | 909PCQT | 1 | VU | 1998-10-09 | 2013-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously Approved 8th Ed (2 February 1995) 9th Ed. for Ser. Nos. 464100 and higher
RP | Watts | 909QT | 0.75 | H | 1998-06-18 | 2013-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously Approved 6th Ed. (15 Jan 1982) 9th Ed. For Ser. Nos. 461650 and higher
RP | Watts | 909QT | 0.75 | VU | 1998-06-18 | 2013-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Serial number 461650 and higher
RP | Watts | 909QT | 1 | H | 1998-06-18 | 2013-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously Approved 6th Ed. (15 Jan 1982) 9th Ed. For Ser. Nos. 461650 and higher
RP | Watts | 909QT | 1 | VU | 1998-06-18 | 2013-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Serial number 461650 and higher
RP | Watts | 909QT | 1.25 | [9 empty] | model designation changed to 909M1QT
RP | Watts | 909QT | 1.5 | [9 empty] | model designation changed to 909M1QT
RP | Watts | 909QT | 2 | [9 empty] | model designation changed to 909M1QT
RP | Watts | 909RW | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 10 | [9 empty] | model designation changed to 909
RP | Watts | 919AQT | 0.75 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919AQT | 1 | VUVD | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919AQT | 1.25 | VUVD | 2006-09-05 | 2012-09-05 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919AQT | 1.5 | VUVD | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919AQT | 2 | VUVD | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 0.75 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 0.75 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.25 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.25 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.5 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.5 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 2 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 2 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 0.75 | VUVU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 1 | VUVU | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 1.25 | VUVU | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 1.5 | VUVU | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 2 | VUVU | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 957 BF | 4 | H | 2008-01-17 | 2014-01-17 | Y | 9 | (yyy) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 BF | 6 | H | 2008-01-17 | 2014-01-17 | Y | 9 | (yyy) | N
RP | Watts | 957N | 2.5 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 2.5 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 3 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 3 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 4 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 4 | VUVD | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 6 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Watts | 957N | 6 | VUVD | 2010-11-15 | 2013-11-15 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Watts | 957N | 8 | VUVD | 2013-06-14 |  | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 957N | 8 | VUVD | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 957NQT | 2.5 | VUVD | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957NQT | 3 | VUVD | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957NQT | 4 | VUVD | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957QT | 2.5 | H | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957QT | 3 | H | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957QT | 4 | H | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 2.5 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 2.5 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 3 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 3 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 4 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 4 | VUVU | 2003-04-14 | 2015-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 8 | VUVU | 2013-06-14 |  | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 957Z | 8 | VUVU | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 957ZQT | 2.5 | VUVU | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957ZQT | 3 | VUVU | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957ZQT | 4 | VUVU | 2009-10-20 | 2012-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 967N | 2.5 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967N | 3 | VUVD | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967N | 4 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Watts | 967N | 4 | VUVD | 2010-11-15 | 2013-11-15 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Watts | 967N | 6 | VUVD | 2013-06-14 |  | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 967N | 6 | VUVD | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 967Z | 2.5 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967Z | 3 | VUVU | 2003-04-14 | 2015-04-14 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967Z | 6 | VUVU | 2013-06-14 |  | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 967Z | 6 | VUVU | 2013-06-14 |  | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 990 | 4 | H | 1992-11-01 | 2013-11-01 | N | 8 | oo,gg,hh,pp,tt,uu,yy | Y
RP | Watts | 990 | 8 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo,gg,hh,pp,tt,uu,yy | Y
RP | Watts | 990QTFDA | 4 | H | 1993-01-13 | 2014-01-13 | N | 8 | ww | Y
RP | Watts | 990QTFDA | 8 | H | 1993-01-13 | 2014-01-13 | N | 8 | ww | Y
RP | Watts | 992 | 4 | H | 1992-11-01 | 2013-11-01 | N | 8 | oo | Y
RP | Watts | 992 | 10 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo | Y
RP | Watts | 995QT | 0.5 | H | 2000-04-13 | 2015-04-13 | N | 9 | int | Y
RP | Watts | 995QT | 0.75 | H | 2000-04-13 | 2015-04-13 | N | 9 | int | Y
RP | Watts | 995QT | 1 | H | 1999-01-14 | 2014-01-14 | N | 9 | int | Y
RP | Watts | 995QT | 1.25 | H | 2002-03-28 | 2014-03-28 | N | 9 | int | Y
RP | Watts | 995QT | 1.5 | H | 2002-03-28 | 2014-03-28 | N | 9 | int | Y
RP | Watts | FAE909HWQT | 1.25 | H | 1980-02-07 | 2013-02-07 | N | 5 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | FAE909HWQT | 1.5 | H | 1980-02-07 | 2013-02-07 | N | 5 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | FAE909HWQT | 2 | H | 1980-02-07 | 2013-02-07 | N | 5 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | FAE909QT | 1.25 | H | 1982-01-15 | 2015-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | FAE909QT | 1.5 | H | 1982-01-15 | 2015-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | FAE909QT | 2 | H | 1982-01-15 | 2015-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | LF009 | 2.5 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (oo) | N
RP | Watts | LF009 | 3 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (oo) | N
RP | Watts | LF009M2PCQT | 1 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2PCQT | 2 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 1 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 1.25 | H | 2008-01-11 | 2014-01-11 | Y | 8 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 1.5 | H | 2008-01-11 | 2014-01-11 | Y | 8 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 2 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M3PCQT | 0.75 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M3QT | 0.75 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009PCQT | 0.5 | H | 2015-03-13 |  | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009QT | 0.5 | H | 2008-01-11 | 2014-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909 | 2.5 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (ll),oo | N
RP | Watts | LF909 | 3 | H | 2010-01-12 | 2013-01-12 | Y | 9 | (ll),oo | N
RP | Watts | LF909 | 4 | H | 2012-07-27 |  | Y | 9 | (ll),oo | N
RP | Watts | LF909 | 6 | H | 2012-07-27 |  | Y | 9 | (ll),oo | N
RP | Watts | LF909M1 | 8 | H | 2010-07-01 | 2013-07-01 | Y | 9 | (ll), oo | N
RP | Watts | LF909M1 | 10 | H | 2010-07-01 | 2013-07-01 | Y | 9 | (ll), oo | N
RP | Watts | LF909M1PCQT | 1.25 | H | 2015-03-13 |  | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1PCQT | 1.5 | H | 2015-03-13 |  | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1PCQT | 2 | H | 2015-03-13 |  | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1QT | 1.25 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1QT | 1.5 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1QT | 2 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 0.75 | H | 2015-03-13 |  | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 0.75 | VU | 2015-03-13 |  | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 1 | H | 2015-03-13 |  | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 1 | VU | 2015-03-13 |  | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909QT | 0.75 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909QT | 0.75 | VU | 2010-11-15 | 2013-11-15 | Y | 9 | (hhhh),rrrrr
RP | Watts | LF909QT | 1 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909QT | 1 | VU | 2010-11-15 | 2013-11-15 | Y | 9 | (hhhh),rrrrr
RP | Watts | LF919AQT | 0.75 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 0.75 | VUVD | 2006-06-14 | 2012-06-14 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919AQT | 1 | VUVD | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 1 | VUVD | 2006-04-12 | 2015-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919AQT | 1.25 | VUVD | 2006-09-05 | 2012-09-05 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 1.25 | VUVD | 2006-09-05 | 2012-09-05 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919AQT | 1.5 | VUVD | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 1.5 | VUVD | 2006-04-12 | 2015-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919AQT | 2 | VUVD | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 2 | VUVD | 2006-04-12 | 2015-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 0.75 | H | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 0.75 | H | 2006-06-14 | 2012-06-14 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 0.75 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 0.75 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1 | H | 2006-04-12 | 2015-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.25 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.25 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.25 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.25 | H | 2006-04-12 | 2015-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.5 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.5 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.5 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.5 | H | 2006-04-12 | 2015-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 2 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 2 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 2 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 2 | H | 2006-04-12 | 2015-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919ZQT | 0.75 | VUVU | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LF919ZQT | 1 | VUVU | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LF919ZQT | 1.25 | VUVU | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LF919ZQT | 1.5 | VUVU | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LF919ZQT | 2 | VUVU | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LFU919AQT | 0.75 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 0.75 | VUVD | 2006-06-14 | 2012-06-14 | Y | 9 | hhhh | N
RP | Watts | LFU919AQT | 1 | VUVD | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 1 | VUVD | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919AQT | 1.25 | VUVD | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 1.25 | VUVD | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919AQT | 1.5 | VUVD | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 1.5 | VUVD | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919AQT | 2 | VUVD | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 2 | VUVD | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1 | H | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.25 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.25 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.25 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.25 | H | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.5 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.5 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.5 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.5 | H | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 2 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 2 | VD | 2006-08-30 | 2012-08-30 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 2 | H | 2006-04-12 | 2015-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 2 | H | 2006-04-12 | 2015-04-12 | Y | 9 | hhhh | N
RP | Watts | SS009M3QT | 0.25 | H | 2001-12-19 | 2013-12-19 | Y | 9 | (hhh) | N
RP | Watts | SS009M3QT | 0.375 | H | 2001-12-19 | 2013-12-19 | Y | 9 | (hhh) | N
RP | Watts | SS009M3QT | 0.5 | H | 2001-12-19 | 2013-12-19 | Y | 9 | (hhh) | N
RP | Watts | SS009M3QT | 0.75 | H | 2001-07-31 | 2013-07-31 | Y | 9 | (hhh) | N
RP | Watts | SS009QT | 1 | H | 1998-05-18 | 2013-05-18 | N | Y | (hhh) | N
RP | Watts | U009APCQT | 0.75 | VDVD | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 0.75 | VDVU | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 0.75 | VUVD | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 0.75 | VUVU | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 1 | VDVD | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009APCQT | 1 | VDVU | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009APCQT | 1 | VUVD | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009APCQT | 1 | VUVU | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 0.75 | VDVD | 1992-06-12 | 2013-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 0.75 | VDVU | 1992-06-12 | 2013-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 0.75 | VUVD | 1992-06-12 | 2013-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 0.75 | VUVU | 1992-06-12 | 2013-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 1 | VDVD | 1992-06-12 | 2013-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 1 | VDVU | 1992-06-12 | 2013-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 1 | VUVD | 1992-06-12 | 2013-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 1 | VUVU | 1992-06-12 | 2013-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VDVD | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VDVU | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VUVD | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VUVU | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VDVD | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VDVU | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VUVD | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VUVU | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VDVD | 1992-12-16 | 2013-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VDVU | 1992-12-16 | 2013-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VUVD | 1992-12-16 | 2013-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VUVU | 1992-12-16 | 2013-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VDVD | 1992-11-09 | 2013-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VDVU | 1992-11-09 | 2013-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VUVD | 1992-11-09 | 2013-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VUVU | 1992-11-09 | 2013-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1PCQT | 1.25 | H | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1QT | 1.25 | H | 1992-06-30 | 2013-06-30 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1QT | 1.5 | H | 1992-06-30 | 2013-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1QT | 2 | H | 1992-06-30 | 2013-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M2APCQT | 1 | VDVD | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1 | VDVU | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1 | VUVD | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1 | VUVU | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VDVD | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VDVU | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VUVD | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VUVU | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VDVD | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VDVU | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VUVD | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VUVU | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VDVD | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VDVU | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VUVD | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VUVU | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VDVD | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VDVU | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VUVD | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VUVU | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VDVD | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VDVU | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VUVD | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VUVU | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2PCQT | 1 | H | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2PCQT | 1.5 | H | 1994-09-12 | 2012-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2PCQT | 2 | H | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 0.75 | H | 1992-11-16 | 2013-11-16 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 1 | H | 1999-01-15 | 2014-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 1.5 | H | 1993-08-24 | 2014-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 2 | H | 1997-08-26 | 2012-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009PCQT | 0.5 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009PCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009PCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009PCQT | 1.25 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009PCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009PCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 0.5 | H | 1995-02-02 | 2013-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009QT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 1.25 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 1.5 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 2 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009SSPCQT | 0.75 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 1 | H | 1993-12-10 | 2014-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 1.25 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 1.5 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 2 | H | 1994-09-27 | 2012-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 0.75 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 1 | H | 1988-01-11 | 2015-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 1.25 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 1.5 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 2 | H | 1988-08-09 | 2012-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | U909HWQT | 0.75 | H | 1979-09-29 | 2012-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U909HWQT | 1 | H | 1979-09-29 | 2012-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U909QT | 0.75 | H | 1998-10-09 | 2013-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | Approved 6th Ed. (15 Jan 1982), 9th Ed. Approval for S/N 464100 and higher
RP | Watts | U909QT | 0.75 | VU | 1998-10-09 | 2013-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | S/N 464100 and greater
RP | Watts | U909QT | 1 | H | 1998-10-09 | 2013-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | Approved 6th Ed. (15 Jan 1982), 9th Ed. Approval for S/N 464100 and higher
RP | Watts | U909QT | 1 | VU | 1998-10-09 | 2013-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | S/N 464100 and greater
RP | Watts | U919AQT | 0.75 | VUVD | 2006-06-14 | 2012-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 1 | VUVD | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 1.25 | VUVD | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 1.5 | VUVD | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 2 | VUVD | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.25 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.25 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.5 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.5 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 2 | H | 2006-06-01 | 2015-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 2 | VD | 2006-08-30 | 2012-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Wilkins | 375 | 0.75 | H | 2007-03-09 | 2013-03-09 | N | 9 | (int) | N
RP | Wilkins | 375 | 1 | H | 2007-03-09 | 2013-03-09 | N | 9 | (int) | N
RP | Wilkins | 375 | 1.25 | H | 2010-04-20 | 2013-04-20 | N | 9 | (int) | N
RP | Wilkins | 375 | 1.5 | H | 2010-04-20 | 2013-04-20 | N | 9 | (int) | N
RP | Wilkins | 375 | 2 | H | 2010-04-20 | 2013-04-20 | N | 9 | (int) | N
RP | Wilkins | 375 | 2.5 | H | 2001-09-28 | 2013-09-28 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 2.5 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 3 | H | 2001-09-28 | 2013-09-28 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 3 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 4 | H | 2000-03-27 | 2015-03-27 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 4 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 6 | H | 2000-07-27 | 2012-07-27 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 6 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 8 | H | 2002-11-11 | 2014-11-11 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 8 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 10 | H | 2004-11-22 | 2013-11-22 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 475 | 2.5 | VUVD | 2002-01-24 | 2014-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 2.5 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 3 | VUVD | 2002-01-24 | 2014-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 3 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 4 | VUVD | 2000-07-27 | 2012-07-27 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 4 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 6 | VUVD | 2000-07-27 | 2012-07-27 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 6 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 8 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 8 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 10 | VUVD | 2004-11-22 | 2013-11-22 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 10 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 975 | 8 | H | 1995-02-06 | 2013-02-06 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975 | 10 | H | 1995-02-06 | 2013-02-06 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375 | 0.5 | H | 2011-04-06 | 2014-04-06 | N | 9 | (int) | N
RP | Wilkins | 375A | 2.5 | H | 2008-10-20 | 2014-10-20 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 2.5 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 3 | H | 2008-10-20 | 2014-10-20 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 3 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 4 | H | 2004-06-02 | 2013-06-02 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 4 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 6 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 6 | H | 2003-11-25 | 2012-11-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 8 | H | 2004-06-15 | 2013-06-15 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 8 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 10 | H | 2007-03-02 | 2013-03-02 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375AMS | 2.5 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 3 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 4 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 6 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 8 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 10 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AR | 2.5 | H | 2010-06-16 | 2013-06-16 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" Up to serial number X18805
RP | Wilkins | 375AR | 2.5 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 3 | H | 2010-06-16 | 2013-06-16 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 3 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 4 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 4 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
RP | Wilkins | 375AR | 6 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 6 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
RP | Wilkins | 375AR | 8 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 8 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
RP | Wilkins | 375AR | 10 | H | 2010-03-25 | 2013-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
RP | Wilkins | 375ARMS | 2.5 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375ARMS | 3 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 48 1/8"
RP | Wilkins | 375ARMS | 4 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
RP | Wilkins | 375ARMS | 6 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
RP | Wilkins | 375ARMS | 8 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
RP | Wilkins | 375ARMS | 10 | H | 2014-11-05 |  | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
RP | Wilkins | 375ARXL | 2.5 | H | 2010-06-16 | 2013-06-16 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375ARXL | 3 | H | 2010-06-16 | 2013-06-16 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
RP | Wilkins | 375ARXL | 4 | H | 2010-06-16 | 2013-06-16 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
RP | Wilkins | 375ARXL | 6 | H | 2010-06-16 | 2013-06-16 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
RP | Wilkins | 375ARXL | 8 | H | 2010-06-16 | 2013-06-16 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
RP | Wilkins | 375ARXL | 10 | H | 2010-06-16 | 2013-06-16 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N |  |  | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
RP | Wilkins | 375AST | 2.5 | H | 2012-06-12 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AST | 3 | H | 2012-06-12 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AST | 4 | H | 2012-05-31 | 2015-05-31 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AST | 6 | H | 2013-06-24 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AST | 8 | H | 2013-11-26 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AST | 10 | H | 2013-11-26 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 2.5 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 3 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 4 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 6 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 8 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 10 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTR | 2.5 | H | 2012-06-12 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375ASTR | 3 | H | 2012-06-12 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
RP | Wilkins | 375ASTR | 4 | H | 2012-05-31 | 2015-05-31 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
RP | Wilkins | 375ASTR | 6 | H | 2013-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
RP | Wilkins | 375ASTR | 8 | H | 2014-01-23 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
RP | Wilkins | 375ASTR | 10 | H | 2014-01-23 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
RP | Wilkins | 375ASTRMS | 2.5 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
RP | Wilkins | 375ASTRMS | 3 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
RP | Wilkins | 375ASTRMS | 4 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
RP | Wilkins | 375ASTRMS | 6 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
RP | Wilkins | 375ASTRMS | 8 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
RP | Wilkins | 375ASTRMS | 10 | H | 2014-11-05 |  | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
RP | Wilkins | 375AXL | 2.5 | H | 2010-04-14 | 2013-04-14 | N | 9 | dddd | N
RP | Wilkins | 375AXL | 2.5 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,yyy,zzz | N
RP | Wilkins | 375AXL | 3 | H | 2010-04-14 | 2013-04-14 | N | 9 | dddd | N
RP | Wilkins | 375AXL | 3 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,yyy,zzz | N
RP | Wilkins | 375AXL | 4 | H | 2010-04-14 | 2013-04-14 | N | 9 | dddd,eeee | N
RP | Wilkins | 375AXL | 4 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 375AXL | 6 | H | 2010-04-14 | 2013-04-14 | N | 9 | dddd,eeee | N
RP | Wilkins | 375AXL | 6 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 375AXL | 8 | H | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 375AXL | 8 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 375AXL | 10 | H | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 375AXL | 10 | H | 2010-02-18 | 2013-02-18 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 375B | 0.5 | H | 2012-11-08 |  | N | 9 | (int) | N
RP | Wilkins | 375B | 0.75 | H | 2012-11-08 |  | N | 9 | (int) | N
RP | Wilkins | 375B | 1 | H | 2012-11-08 |  | N | 9 | (int) | N
RP | Wilkins | 375B | 1.25 | H | 2012-11-08 |  | N | 9 | (int) | N
RP | Wilkins | 375B | 1.5 | H | 2012-11-08 |  | N | 9 | (int) | N
RP | Wilkins | 375B | 2 | H | 2012-11-08 |  | N | 9 | (int) | N
RP | Wilkins | 375MS | 2.5 | H | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 2.5 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 3 | H | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 3 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 4 | H | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 4 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 6 | H | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 6 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,zzz,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 8 | H | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 8 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 10 | H | 2005-03-29 | 2014-03-29 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375ST | 0.5 | H | 2011-02-22 | 2014-02-22 | Y | 9 | (int) | N
RP | Wilkins | 375ST | 0.75 | H | 2011-02-22 | 2014-02-22 | Y | 9 | (int) | N
RP | Wilkins | 375ST | 1 | H | 2011-10-31 | 2014-10-31 | Y | 9 | int | N
RP | Wilkins | 375XL | 0.5 | H | 2009-04-07 | 2015-04-07 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 0.75 | H | 2007-03-09 | 2013-03-09 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 1 | H | 2007-03-09 | 2013-03-09 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 1.25 | H | 2010-04-20 | 2013-04-20 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 1.5 | H | 2010-04-20 | 2013-04-20 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 2 | H | 2010-04-20 | 2013-04-20 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 2.5 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 375XL | 2.5 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XL | 3 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 375XL | 3 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XL | 4 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
RP | Wilkins | 375XL | 4 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XL | 6 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
RP | Wilkins | 375XL | 6 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XL | 8 | H | 2010-02-18 | 2013-02-18 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
RP | Wilkins | 375XL | 8 | H | 2010-02-18 | 2013-02-18 | Y | 9 | gg,hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XL | 10 | H | 2010-02-18 | 2013-02-18 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
RP | Wilkins | 375XL | 10 | H | 2010-02-18 | 2013-02-18 | Y | 9 | gg,hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XLB | 0.5 | H | 2012-11-08 |  | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 0.75 | H | 2012-11-08 |  | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 1 | H | 2012-11-08 |  | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 1.25 | H | 2012-11-08 |  | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 1.5 | H | 2012-11-08 |  | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 2 | H | 2012-11-08 |  | Y | 9 | (int) | N
RP | Wilkins | 375XLMS | 2.5 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 375XLMS | 2.5 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XLMS | 3 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 375XLMS | 3 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XLMS | 4 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zzzzz,dddd,eeee | N
RP | Wilkins | 375XLMS | 4 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XLMS | 6 | H | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,dddd,eeee | N
RP | Wilkins | 375XLMS | 6 | H | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,zzz,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XLMS | 8 | H | 2010-02-18 | 2013-02-18 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
RP | Wilkins | 375XLMS | 8 | H | 2010-02-18 | 2013-02-18 | Y | 9 | gg,hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 375XLMS | 10 | H | 2010-02-18 | 2013-02-18 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd,eeee | N
RP | Wilkins | 375XLMS | 10 | H | 2010-02-18 | 2013-02-18 | Y | 9 | gg,hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 475MS | 2.5 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 2.5 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 3 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 3 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 4 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 4 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 6 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 6 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 8 | VUVD | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 8 | VUVD | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 10 | H | 2005-03-29 | 2014-03-29 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 2.5 | VUVU | 2002-01-24 | 2014-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 2.5 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 3 | VUVU | 2002-01-24 | 2014-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 3 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 4 | VUVU | 2000-09-09 | 2012-09-09 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 4 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 6 | VUVU | 2001-05-31 | 2013-05-31 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 6 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 8 | VUVU | 2004-06-08 | 2013-06-08 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 8 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 10 | VUVU | 2004-11-22 | 2013-11-22 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 10 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 2.5 | VUVU | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 2.5 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 3 | VUVU | 2003-07-03 | 2012-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 3 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 4 | VUVU | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 4 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 6 | VUVU | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 6 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 8 | VUVU | 2003-07-03 | 2012-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 8 | VUVU | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 10 | H | 2005-03-29 | 2014-03-29 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 10 | H | 2010-09-09 | 2013-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475XL | 2.5 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XL | 2.5 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XL | 3 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XL | 3 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XL | 4 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XL | 4 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XL | 6 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XL | 6 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XL | 8 | VUVD | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XL | 8 | VUVD | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XL | 10 | VUVD | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XL | 10 | VUVD | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLMS | 2.5 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XLMS | 2.5 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLMS | 3 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XLMS | 3 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLMS | 4 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLMS | 4 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLMS | 6 | VUVD | 2010-04-14 | 2013-04-14 | N | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLMS | 6 | VUVD | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLMS | 8 | VUVD | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLMS | 8 | VUVD | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLMS | 10 | H | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLMS | 10 | H | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLV | 2.5 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XLV | 2.5 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLV | 3 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XLV | 3 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLV | 4 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLV | 4 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLV | 6 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLV | 6 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLV | 8 | VUVU | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLV | 8 | VUVU | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLV | 10 | VUVU | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLV | 10 | VUVU | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLVMS | 2.5 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XLVMS | 2.5 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLVMS | 3 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | ee,ff,ll,mm,tt,uu,yy,zz,zzz,dddd | N
RP | Wilkins | 475XLVMS | 3 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLVMS | 4 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLVMS | 4 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLVMS | 6 | VUVU | 2010-04-14 | 2013-04-14 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLVMS | 6 | VUVU | 2010-04-14 | 2013-04-14 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLVMS | 8 | VUVU | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLVMS | 8 | VUVU | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 475XLVMS | 10 | H | 2010-02-18 | 2013-02-18 | N | 9 | zzz,dddd,eeee | N
RP | Wilkins | 475XLVMS | 10 | H | 2010-02-18 | 2013-02-18 | Y | 9 | ppp,qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | N
RP | Wilkins | 575 | 0.75 | H | 1976-04-28 | 2015-04-28 | N | 5 |  | Y
RP | Wilkins | 575 | 1 | H | 1976-04-28 | 2015-04-28 | N | 5 |  | Y
RP | Wilkins | 575 | 2.5 | H | 1986-09-25 | 2013-09-25 | N | 7 | gg,ee,tt,yy | Y
RP | Wilkins | 575 | 3 | H | 1979-08-20 | 2012-08-20 | N | 5 | gg,ee,tt,yy | Y
RP | Wilkins | 575 | 4 | H | 1980-06-08 | 2013-06-08 | N | 5 | gg,ee,tt,yy | Y
RP | Wilkins | 575 | 6 | H | 1981-07-06 | 2014-07-06 | N | 6 | gg,ee,tt,yy | Y
RP | Wilkins | 575 (MOD-III) | 1.25 | H | 1976-10-11 | 2012-10-11 | N | 5 | ii | Y
RP | Wilkins | 575 (MOD-III) | 1.5 | H | 1976-10-11 | 2012-10-11 | N | 5 | ii | Y
RP | Wilkins | 575 (MOD-III) | 2 | H | 1976-10-11 | 2012-10-11 | N | 5 | ii | Y
RP | Wilkins | 575A | 0.75 | H | 1987-04-17 | 2014-04-17 | N | 7 | ii | Y
RP | Wilkins | 575A | 1 | H | 1987-04-17 | 2014-04-17 | N | 7 | ii | Y
RP | Wilkins | 575M10 | 10 | H | 1983-06-01 | 2013-06-01 | N | 6 | gg,ee,tt,yy | Y |  |  | 6"x6"x10" manifold, formerly MBC-10"
RP | Wilkins | 575M8 | 8 | H | 1983-04-11 | 2013-04-11 | N | 6 | gg,ee,tt,yy | Y |  |  | 4"x4"x8" manifold, formerly MBC-8"
RP | Wilkins | 975 | 0.75 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 1 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 1.25 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 1.5 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 2 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 2.5 | H | 1991-11-26 | 2012-11-26 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975 | 3 | H | 1991-11-08 | 2012-11-08 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975 | 4 | H | 1991-11-08 | 2012-11-08 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975 | 6 | H | 1991-11-08 | 2012-11-08 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975A | 0.75 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 1 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 1.25 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 1.5 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 2 | H | 1991-07-18 | 2012-07-18 | N | 8 | ii | Y
RP | Wilkins | 975BMS | 2.5 | H | 1997-06-17 | 2012-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975BMS | 3 | H | 1997-06-17 | 2012-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975BMS | 4 | H | 1997-06-17 | 2012-06-17 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975BMS | 6 | H | 1997-06-17 | 2012-06-17 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975BMS | 8 | H | 1997-06-17 | 2012-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975BMS | 10 | H | 1997-06-17 | 2012-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975MS | 2.5 | H | 1995-05-05 | 2013-05-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975MS | 3 | H | 1995-05-05 | 2013-05-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975MS | 4 | H | 1995-05-05 | 2013-05-05 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 6 | H | 1995-05-05 | 2013-05-05 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 8 | H | 1996-12-05 | 2014-12-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975MS | 10 | H | 1996-12-05 | 2014-12-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | N
RP | Wilkins | 975XL | 0.25 | H | 1994-07-12 | 2012-07-12 | N | 8 | (ii) | N
RP | Wilkins | 975XL | 0.375 | H | 1994-07-12 | 2012-07-12 | N | 8 | (ii) | N
RP | Wilkins | 975XL | 0.5 | H | 1994-07-12 | 2012-07-12 | N | 8 | (ii) | N
RP | Wilkins | 975XL | 0.75 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XL | 1 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XL | 1.25 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo,ggg | N
RP | Wilkins | 975XL | 1.5 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XL | 2 | H | 1992-11-02 | 2013-11-02 | N | 8 | (ii),bbb,ooo,bbbbb,ccccc | N
RP | Wilkins | 975XL2 | 0.25 | H | 2009-10-01 | 2012-10-01 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 0.375 | H | 2009-10-01 | 2012-10-01 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 0.5 | H | 2009-10-01 | 2012-10-01 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 0.75 | H | 2009-07-29 | 2012-07-29 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 1 | H | 2009-07-29 | 2012-07-29 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 1.25 | H | 2009-08-21 | 2012-08-21 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 1.5 | H | 2009-08-21 | 2012-08-21 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 2 | H | 2009-08-21 | 2012-08-21 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 0.75 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 1 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 1.25 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 1.5 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 2 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 0.75 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 1 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 1.25 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 1.5 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 2 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2SE | 0.75 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 0.75 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1.25 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1.25 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1.5 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1.5 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 2 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 2 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SEU | 0.75 | VUVD | 2011-03-29 | 2014-03-29 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 0.75 | VUVU | 2011-03-29 | 2014-03-29 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1 | VUVD | 2011-03-29 | 2014-03-29 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1 | VUVU | 2011-03-29 | 2014-03-29 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1.25 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1.25 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1.5 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1.5 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 2 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 2 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2TCU | 0.5 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2TCU | 0.75 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2TCU | 1 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2TCU | 1.25 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2TCU | 1.5 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2TCU | 2 | H | 2010-09-09 | 2013-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2U | 0.75 | H | 2011-02-22 | 2014-02-22 | Y | 8 | (mmmmm) | N
RP | Wilkins | 975XL2U | 1 | H | 2011-02-22 | 2014-02-22 | Y | 8 | (mmmmm) | N
RP | Wilkins | 975XL2U | 1.5 | H | 2011-02-22 | 2014-02-22 | Y | 8 | (mmmmm) | N
RP | Wilkins | 975XL2U | 2 | H | 2011-02-22 | 2014-02-22 | Y | 8 | (mmmmm) | N
RP | Wilkins | 975XL2V | 0.75 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2V | 0.75 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2V | 1 | VUVD | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2V | 1 | VUVU | 2011-02-22 | 2014-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XLBF | 2 | H | 2011-02-22 | 2014-02-22 | N | 8 | (bbbbb) | N
RP | Wilkins | 975XLBFSS | 2 | H | 2011-02-22 | 2014-02-22 | N | 8 | (ccccc) | N
RP | Wilkins | 975XLBMS | 0.75 | H | 1997-05-09 | 2015-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 1 | H | 1997-05-09 | 2015-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 1.25 | H | 1997-05-09 | 2015-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 1.5 | H | 1997-05-09 | 2015-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 2 | H | 1997-05-09 | 2015-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLD | 0.75 | H | 2002-10-08 | 2014-10-08 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLD | 0.75 | H | 2013-07-03 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XLMS | 0.75 | H | 1994-08-30 | 2012-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 1 | H | 1994-08-30 | 2012-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 1.25 | H | 1994-08-30 | 2012-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 1.5 | H | 1994-08-30 | 2012-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 2 | H | 1994-08-30 | 2012-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLSE | 0.75 | VUVD | 2000-10-16 | 2012-10-16 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 0.75 | VUVU | 2000-10-16 | 2012-10-16 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1 | VUVD | 2000-10-16 | 2012-10-16 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1 | VUVU | 2000-10-16 | 2012-10-16 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1.25 | VUVD | 1999-11-04 | 2014-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1.25 | VUVU | 1999-11-04 | 2014-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1.5 | VUVD | 1999-11-04 | 2014-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1.5 | VUVU | 1999-11-04 | 2014-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 2 | VUVD | 1999-11-04 | 2014-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 2 | VUVU | 1999-11-04 | 2014-11-04 | N | 9 | (ii).ooo | N
RP | Wilkins | 975XLSEU | 0.75 | VUVD | 2000-10-16 | 2012-10-16 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 0.75 | VUVU | 2000-10-16 | 2012-10-16 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 1 | VUVD | 2000-10-16 | 2012-10-16 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 1 | VUVU | 2000-10-16 | 2012-10-16 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 1.25 | VUVD | 2000-03-27 | 2015-03-27 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 1.25 | VUVU | 2000-03-27 | 2015-03-27 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 1.5 | VUVD | 2000-03-27 | 2015-03-27 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 1.5 | VUVU | 2000-03-27 | 2015-03-27 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 2 | VUVD | 2000-03-27 | 2015-03-27 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLSEU | 2 | VUVU | 2000-03-27 | 2015-03-27 | N | 9 | (ggg),xxx | N
RP | Wilkins | 975XLST | 0.375 | H | 2002-11-19 | 2014-11-19 | Y | 9 | (ggggg) | N
RP | Wilkins | 975XLST | 0.5 | H | 2002-11-19 | 2014-11-19 | Y | 9 | (ggggg) | N
RP | Wilkins | 975XLTCU | 0.5 | H | 2007-04-05 | 2013-04-05 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLTCU | 0.75 | H | 2006-06-27 | 2012-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLTCU | 1 | H | 2006-06-27 | 2012-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLTCU | 1.25 | H | 2006-06-27 | 2012-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLTCU | 1.5 | H | 2006-06-27 | 2012-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLTCU | 2 | H | 2006-06-27 | 2012-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLU | 0.75 | H | 1993-09-02 | 2014-09-02 | N | 8 | (ggg),xxx | N
RP | Wilkins | 975XLU | 1 | H | 1993-09-02 | 2014-09-02 | N | 8 | (ggg),xxx | N
RP | Wilkins | 975XLU | 1.5 | H | 1993-09-02 | 2014-09-02 | N | 8 | (ggg),xxx | N
RP | Wilkins | 975XLU | 2 | H | 1993-09-02 | 2014-09-02 | N | 8 | (ggg),xxx | N
RP | Wilkins | 975XLV | 0.75 | VUVD | 2001-01-07 | 2013-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLV | 0.75 | VUVU | 2001-01-07 | 2013-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLV | 1 | VUVD | 2001-01-07 | 2013-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLV | 1 | VUVU | 2001-01-07 | 2013-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | MBC-10" | 10 | [9 empty] | 6"x6"x10" manifold, Model designation changed to 575M10
RP | Wilkins | MBC-8" | 8 | [9 empty] | 6"x6"x10" manifold,Model designation changed to 575M8
RP | Apollo/Conbraco | RPLF4AN | 4 | VUVU | 2014-06-11 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4AN | 6 | VUVD | 2014-06-10 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RP | Apollo/Conbraco | RPLF4AN | 6 | VUVU | 2014-06-11 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N
RPDA | Ames | 5000 | 4 | H | 1989-12-28 | 2013-12-20 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Conbraco 4020402 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Ames | 5000 | 6 | H | 1989-12-28 | 2013-12-20 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Conbraco 4020402 3/4 (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q
RPDA | Ames | 5000 | 8 | H | 1989-07-01 | 2013-07-01 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Conbraco 4020402 3/4 (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q
RPDA | Ames | 5000 | 10 | H | 1990-03-19 | 2014-03-19 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Conbraco 4020402 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Ames | 5000CIV | 2.5 | H | 2000-07-07 | 2012-07-07 | N | 8 | (pp),hh,mm,uu | N | Watts 909QT 3/4 (H) | (H),C,D,E,F,G,I,J,K,L,M,N,O,P,Q
RPDA | Ames | 5000CIV | 3 | H | 2000-07-07 | 2012-07-07 | N | 8 | (pp),hh,mm,uu,eee | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | 5000CIV | 4 | H | 2000-07-07 | 2012-07-07 | N | 8 | (pp),hh,mm,uu,eee | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | 5000CIV | 6 | H | 2000-07-07 | 2012-07-07 | N | 8 | (pp),hh,mm,uu,eee | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | 5000CIV | 8 | H | 2000-07-07 | 2012-07-07 | N | 8 | (pp),hh,mm,uu,eee | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | 5000CIV | 10 | H | 2000-07-07 | 2012-07-07 | N | 8 | (pp),hh,mm,uu,eee | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 2.5 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 3 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 4 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 6 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 8 | H | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 10 | H | 2010-09-27 | 2013-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 2.5 | VUVD | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 3 | VUVD | 2009-05-28 | 2015-05-28 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 4 | VUVD | 2009-05-28 | 2015-05-28 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 8 | VUVD | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 2.5 | VUVD | 2009-05-28 | 2015-05-28 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 6 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 8 | VUVD | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 3 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 4 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 8 | VUVU | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 3 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 4 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 8 | VUVU | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | LFColt 500-GV | 2.5 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500-GV | 3 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500-GV | 4 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500-GV | 6 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 2.5 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 3 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 4 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 6 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NBF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NBF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NBF | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NGV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NGV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NGV | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZBF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZBF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZBF | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZGV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZGV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZGV | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 2.5 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 3 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 4 | H | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NBF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NBF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NGV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NGV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZBF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZBF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZGV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZGV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | Maxim 500-GV | 2.5 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 3 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 4 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 6 | H | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 8 | H | 2010-09-27 | 2013-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 10 | H | 2010-09-27 | 2013-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 2.5 | VUVD | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 4 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 6 | VUVD | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 4 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 6 | VUVD | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZBF | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZBF | 3 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZBF | 6 | VUVU | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZGV | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZGV | 3 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZGV | 6 | VUVU | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Apollo/Conbraco | 4070003 | 3 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 40700C3 | 3 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 40700E3 | 3 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070A03 | 4 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070AE3 | 4 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070C03 | 6 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070CC3 | 6 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070CE3 | 6 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070E03 | 8 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070EC3 | 8 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070EE3 | 8 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070G03 | 10 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070GC3 | 10 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 4070GE3 | 10 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | 407AC3 | 4 | [9 empty] | model designation changed to RPDA40
RPDA | Apollo/Conbraco | RPDA40 | 3 | H | 1993-07-27 | 2014-07-27 | N | 8 | (uu),cc,mm | Y | Apollo/Conbraco 4020402 3/4" (H), Apollo/Conbraco RP40 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4070003, 40700C3, 40700E3
RPDA | Apollo/Conbraco | RPDA40 | 4 | H | 1993-07-27 | 2014-07-27 | N | 8 | (uu),cc,mm | N | Apollo/Conbraco 4020402 3/4" (H), Apollo/Conbraco RP40 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4070A03, 407AC3, 4070AE3
RPDA | Apollo/Conbraco | RPDA40 | 6 | H | 1993-10-20 | 2014-10-20 | N | 8 | (uu),cc,mm | N | Apollo/Conbraco 4020402 3/4" (H), Apollo/Conbraco RP40 3/4" (H) | (M),D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4070C03, 4070CC3, 4070CE3
RPDA | Apollo/Conbraco | RPDA40 | 8 | H | 1993-05-24 | 2014-05-24 | N | 8 | (uu),cc,mm | N | Apollo/Conbraco 4020402 3/4" (H), Apollo/Conbraco RP40 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4070E03, 4070EC3, 4070EE3
RPDA | Apollo/Conbraco | RPDA40 | 10 | H | 1993-04-13 | 2014-04-13 | N | 8 | (uu),cc,mm | N | Apollo/Conbraco 4020402 3/4" (H), Apollo/Conbraco RP40 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 4070G03, 4070GC3, 4070GE3
RPDA | Apollo/Conbraco | RPDALF4A | 2.5 | H | 2014-06-10 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (P),O
RPDA | Apollo/Conbraco | RPDALF4A | 3 | H | 2014-06-10 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (P),O
RPDA | Apollo/Conbraco | RPDALF4A | 4 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
RPDA | Apollo/Conbraco | RPDALF4A | 6 | H | 2013-06-24 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
RPDA | Apollo/Conbraco | RPDALF4AN | 4 | VUVD | 2014-06-10 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
RPDA | Apollo/Conbraco | RPDALF4AN | 4 | VUVU | 2014-06-11 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q
RPDA | Apollo/Conbraco | RPDALF4AN | 6 | VUVD | 2015-05-12 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L, N,O,P,Q
RPDA | Apollo/Conbraco | RPDALF4AN | 6 | VUVU | 2015-05-12 |  | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L, N,O,P,Q
RPDA | Cla-Val | 18-4 | 10 | H | 1990-08-23 | 2014-08-23 | N | 8 | hh,gg,qq,rr | Y | Cla-Val RP2 3/4 (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q
RPDA | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
RPDA | Febco | 826 Type YD | 2.5 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 3 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 4 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 6 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 8 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 10 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826YD | 2.5 | H | 1988-11-11 | 2012-11-11 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 825Y 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 826 Type YD
RPDA | Febco | 826YD | 3 | H | 1988-11-11 | 2012-11-11 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 825Y 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 826 Type YD
RPDA | Febco | 826YD | 4 | H | 1988-10-14 | 2012-10-14 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 825Y 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 826 Type YD
RPDA | Febco | 826YD | 6 | H | 1990-03-01 | 2014-03-01 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 825Y 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 826 Type YD
RPDA | Febco | 826YD | 8 | H | 1990-06-22 | 2014-06-22 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 825Y 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 826 Type YD
RPDA | Febco | 826YD | 10 | H | 1990-06-22 | 2014-06-22 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 825Y 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q | formerly 826 Type YD
RPDA | Neptune | [5 empty] | N | [5 empty] | See Wilkins
RPDA | Watts | 009NRSRPDA | 4 | H | 1995-02-01 | 2013-02-01 | N | 8 | oo,gg,ll,tt | Y | Watts 009M2QT 3/4 (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 009NRSRPDA | 6 | H | 1995-02-01 | 2013-02-01 | N | 8 | oo,gg,ll,tt | Y | Watts 009M2QT 3/4 (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 009OSYRPDA | 4 | H | 1995-02-01 | 2013-02-01 | N | 8 | pp,hh,mm,uu,zz | Y | Watts 009M2QT 3/4 (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 009OSYRPDA | 6 | H | 1995-02-01 | 2013-02-01 | N | 8 | pp,hh,mm,uu,zz | Y | Watts 009M2QT 3/4 (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 909DDC | 6 | [9 empty] | model designation changed to 909RPDA
RPDA | Watts | 909DDCM2 | 3 | [9 empty] | model designation changed to 909RPDA
RPDA | Watts | 909RPDA | 2.5 | H | 1999-06-16 | 2014-06-16 | N | 8 | (pp),hh,mm,uu,zz,ffff,gggg | N | Watts 909QT 3/4 (H) | (H),C,D,E,F,G,H,I,J,K,L,M,O,P,Q
RPDA | Watts | 909RPDA | 3 | H | 1988-10-05 | 2012-10-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q | formerly 909DDCM2
RPDA | Watts | 909RPDA | 4 | H | 1988-02-09 | 2015-02-01 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q
RPDA | Watts | 909RPDA | 6 | H | 1988-10-05 | 2012-10-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q | formerly 909DDC
RPDA | Watts | 909RPDA | 8 | H | 1988-02-14 | 2015-02-14 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q
RPDA | Watts | 909RPDA | 10 | H | 1988-02-15 | 2015-02-15 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q
RPDA | Watts | 957NRPDA-BF | 2.5 | VUVD | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-BF | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-BF | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-BF | 8 | VUVD | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 4 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 6 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 8 | VUVD | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957RPDA-GV | 2.5 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 3 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 4 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 6 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 8 | H | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957RPDA-GV | 10 | H | 2010-09-27 | 2013-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957ZRPDA-BF | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-BF | 3 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-BF | 4 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-BF | 8 | VUVU | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 3 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 4 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 8 | VUVU | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 2.5 | VUVD | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 4 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 6 | VUVD | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 2.5 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 3 | VUVD | 2009-04-07 | 2015-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 4 | VUVD | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 6 | VUVD | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967RPDA-GV | 2.5 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 3 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 4 | H | 2006-06-20 | 2012-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 6 | H | 2010-11-15 | 2013-11-15 | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967RPDA-GV | 8 | H | 2010-09-27 | 2013-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 10 | H | 2010-09-27 | 2013-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967ZRPDA-BF | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-BF | 3 | VUVU | 2013-06-24 |  | N | 9 | (yyy) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-BF | 6 | VUVU | 2013-06-14 |  | N | 9 | (yyy) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-GV | 2.5 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-GV | 3 | VUVU | 2013-06-24 |  | N | 9 | (zzz) | N | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-GV | 6 | VUVU | 2013-06-14 |  | N | 9 | (zzz) |  | Watts 919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 990RPDA | 4 | H | 1992-11-01 | 2013-11-11 | N | 8 | pp,hh,mm,uu,zz | Y | Watts 009QT 3/4 (H) | (H),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 990RPDA | 8 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu | Y | Watts 009QT 3/4 (H) | (H),D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 992RPDA | 4 | H | 1992-11-01 | 2013-11-11 | N | 8 | oo | Y | Watts 009QT 3/4 (H) | (H),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 992RPDA | 10 | H | 1993-01-13 | 2014-01-13 | N | 8 | oo | Y | Watts 009QT 3/4 (H) | (H),D,E,F,G,H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | LF957NRPDA-BF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-BF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-BF | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-GV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-GV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-GV | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957RPDA-GV | 2.5 | H | 2014-05-15 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDA-GV | 3 | H | 2014-05-15 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDA-GV | 4 | H | 2014-05-15 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDA-GV | 6 | H | 2014-05-15 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957ZRPDA-BF | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-BF | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-BF | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-GV | 2.5 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-GV | 3 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-GV | 4 | VUVD | 2014-01-08 |  | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 2.5 | H | 2008-10-20 | 2014-10-20 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ADA | 2.5 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 3 | H | 2008-10-20 | 2014-10-20 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ADA | 3 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 4 | H | 2004-06-02 | 2013-06-02 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ADA | 4 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 6 | H | 2003-11-25 | 2012-11-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ADA | 6 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 8 | H | 2004-06-15 | 2013-06-15 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (N), G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ADA | 8 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 10 | H | 2009-03-11 | 2015-03-11 | N | 9 | (qqq), ttt, www, yyy, zzz, eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Wilkins | 375ADA | 10 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 2.5 | H | 2010-06-16 | 2013-06-16 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
RPDA | Wilkins | 375ADAR | 2.5 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 3 | H | 2010-06-16 | 2013-06-16 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
RPDA | Wilkins | 375ADAR | 3 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 4 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
RPDA | Wilkins | 375ADAR | 4 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 6 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
RPDA | Wilkins | 375ADAR | 6 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 8 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86"
RPDA | Wilkins | 375ADAR | 8 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 10 | H | 2010-03-25 | 2013-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,M,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
RPDA | Wilkins | 375ADAR | 10 | H | 2014-02-18 |  | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 2.5 | H | 2013-06-14 |  | N | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ASTDA | 2.5 | H | 2014-02-20 |  | Y | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 3 | H | 2013-06-14 |  | N | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ASTDA | 3 | H | 2014-02-20 |  | Y | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 4 | H | 2013-06-14 |  | N | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ASTDA | 4 | H | 2014-02-20 |  | Y | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 6 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M
RPDA | Wilkins | 375ASTDA | 8 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M
RPDA | Wilkins | 375ASTDA | 10 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O)
RPDA | Wilkins | 375ASTDAR | 3 | H | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
RPDA | Wilkins | 375ASTDAR | 4 | H | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
RPDA | Wilkins | 375ASTDAR | 6 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
RPDA | Wilkins | 375ASTDAR | 8 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
RPDA | Wilkins | 375ASTDAR | 10 | H | 2014-09-18 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O) | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
RPDA | Wilkins | 375ASTDAR | 2 1/2" | H | 2014-10-09 |  | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
RPDA | Wilkins | 375DA | 2.5 | H | 2002-10-08 | 2014-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375DA | 2.5 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 3 | H | 2002-10-08 | 2014-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375DA | 3 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 4 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 4 | H | 2000-12-13 | 2012-12-13 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375DA | 6 | H | 2001-05-31 | 2013-05-31 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 975XLD 3/4 (H) | (N),C,D,E,F,G,H,I,J,K,L,M,O,P,Q
RPDA | Wilkins | 375DA | 6 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 8 | H | 2004-06-15 | 2013-06-15 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 975XLD 3/4" (H) | (N), G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375DA | 8 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 10 | H | 2004-11-22 | 2013-11-22 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk | N | Wilkins 975XLD 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q
RPDA | Wilkins | 375DA | 10 | H | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DA | 4 | VUVD | 2001-03-20 | 2013-03-20 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q
RPDA | Wilkins | 475DA | 4 | VUVD | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DA | 6 | VUVD | 2001-05-31 | 2013-05-31 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q
RPDA | Wilkins | 475DA | 6 | VUVD | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DA | 8 | VUVD | 2004-08-11 | 2013-08-11 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 475DA | 8 | VUVD | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DAV | 4 | VUVU | 2001-03-20 | 2013-03-20 | N | 9 | (qqq),mm,ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q
RPDA | Wilkins | 475DAV | 4 | VUVU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DAV | 6 | VUVU | 2004-07-20 | 2013-07-20 | N | 9 | (qqq),mm,ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q
RPDA | Wilkins | 475DAV | 6 | VUVU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DAV | 8 | VUVU | 2004-04-24 | 2013-04-24 | N | 9 | (qqq),mm,ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 975XLD 3/4 (H) | (M), B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 475DAV | 8 | VUVU | 2014-02-18 |  | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 975DA | 2.5 | H | 1994-02-01 | 2015-02-01 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy,zzzz | N | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 975DA | 3 | H | 1994-02-01 | 2015-02-01 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy,zzzz | N | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 975DA | 4 | H | 1993-11-01 | 2014-11-01 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 975DA | 6 | H | 1994-03-14 | 2015-03-14 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 975DA | 8 | H | 1996-12-05 | 2014-12-05 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy.zzzz | N | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 975DA | 10 | H | 1996-12-05 | 2014-12-05 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy.zzzz | N | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q
RPDA-II | Febco | LF866 | 2.5 | H | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF866 | 2.5 | VU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF866 | 3 | H | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF866 | 3 | VU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF866 | 4 | H | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF866 | 6 | H | 2015-03-13 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 2.5 | VUVD | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 2.5 | VUVU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 3 | VUVD | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 3 | VUVU | 2015-03-20 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 4 | VUVD | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 4 | VUVU | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 6 | VUVD | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 6 | VUVU | 2015-01-26 |  | N | 10 | (mm), ll | N | Watts 3/4" LF619 (HVD) | (O),J,K,L,M,N,P,Q
SVB | Apollo/Conbraco | SVB | 0.25 | [9 empty] | model designation changed to SVB4W
SVB | Apollo/Conbraco | SVB | 0.375 | [9 empty] | model designation changed to SVB4W
SVB | Apollo/Conbraco | SVB | 0.5 | [9 empty] | model designation changed to SVB4W
SVB | Apollo/Conbraco | SVB4W | 0.25 | H | 2000-11-30 | 2012-11-30 | N | 9 | (int) | N |  |  | formerly SVB
SVB | Apollo/Conbraco | SVB4W | 0.375 | H | 2000-11-30 | 2012-11-30 | N | 9 | (int) | N |  |  | formerly SVB
SVB | Apollo/Conbraco | SVB4W | 0.5 | H | 2000-11-30 | 2012-11-30 | N | 9 | (int) | N |  |  | formerly SVB
SVB | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
SVB | Watts | 008PCQT | 0.375 | VUH | 1998-11-18 | 2013-11-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
SVB | Watts | 008PCQT | 0.5 | VUH | 1998-11-18 | 2013-11-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Watts | 008PCQT | 0.75 | VUH | 2000-06-19 | 2012-06-19 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Watts | 008PCQT | 1 | VUH | 2000-06-19 | 2012-06-19 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Watts | LF008PCQT | 0.375 | VUH | 2015-03-13 |  | Y | 9 | (vv),xx,ooo,hhhh,pppp | N
SVB | Watts | LF008PCQT | 0.5 | VUH | 2015-03-13 |  | Y | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Watts | LF008PCQT | 0.75 | VUH | 2015-03-13 |  | Y | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Watts | LF008PCQT | 1 | VUH | 2015-03-13 |  | Y | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Wilkins | 460 | 0.375 | VUH | 2007-03-09 | 2013-03-09 | N | 9 | (ooo),ii | N
SVB | Wilkins | 460 | 0.5 | VUH | 2007-03-09 | 2013-03-09 | N | 9 | (ooo),ii | N
SVB | Wilkins | 460 | 0.75 | VUH | 2008-05-08 | 2014-05-08 | N | 9 | (ooo),ii | N
SVB | Wilkins | 460 | 1 | VUH | 2008-05-08 | 2014-05-08 | N | 9 | (ooo),ii | N
SVB | Wilkins | 460XL | 0.375 | VUH | 2011-03-21 | 2014-03-21 | Y | 9 | (iiii) | N
SVB | Wilkins | 460XL | 0.5 | VUH | 2011-03-21 | 2014-03-21 | Y | 9 | (iiii) | N
SVB | Wilkins | 460XL | 0.75 | VUH | 2011-03-21 | 2014-03-21 | Y | 9 | (iiii) | N
SVB | Wilkins | 460XL | 1 | VUH | 2011-03-21 | 2014-03-21 | Y | 9 | (iiii) | N

## Recent Changes
List of Approved Backflow Prevention Assemblies
4 June 2015
Supersedes All Prior Lists
Foundation for Cross-Connection Control | [7 empty] | 2015 © University of Southern California
and Hydraulic Research
a D I v i s I o n o f t h e U n I v e r s I t y o f S o u t h e r n C a l I f o r n I a
ADDITIONS
Double Check Valve Assemblies
| Type | Manufacturer | Model | Size | Orientation(s) | Approved
| DC | Apollo/Conbraco | DCLF4SG | 2.5 | H | 2015-01-23
| DC | Apollo/Conbraco | DCLF4SG | 2.5 | VU | 2015-01-23
| DC | Apollo/Conbraco | DCLF4SG | 3 | H | 2015-01-23
| DC | Apollo/Conbraco | DCLF4SG | 3 | VU | 2015-01-23
| DC | Apollo/Conbraco | DCLF4SG | 4 | H | 2015-01-23
| DC | Apollo/Conbraco | DCLF4SG | 4 | VU | 2015-01-23
| DC | Apollo/Conbraco | DCLF4SG | 6 | H | 2015-01-23
| DC | Apollo/Conbraco | DCLF4SG | 6 | VU | 2015-01-23
| DC | Watts | LF007M1PCQT | 1 | H | 2015-03-13
| DC | Watts | LF007M1PCQT | 1 | VU | 2015-03-13
| DC | Watts | LF007M1PCQT | 2 | H | 2015-03-13
| DC | Watts | LF007M1PCQT | 2 | VU | 2015-03-13
| DC | Watts | LF007M3PCQT | 0.75 | H | 2015-03-13
| DC | Watts | LF007M3PCQT | 0.75 | VU | 2015-03-13
| DC | Watts | LF007PCQT | 0.5 | H | 2015-03-13
| DC | Watts | LF007PCQT | 0.5 | VU | 2015-03-13
Reduced Pressure Priciple Assemblies
| RP | Watts | LF009M2PCQT | 1 | H | 2015-03-13
| RP | Watts | LF009M2PCQT | 2 | H | 2015-03-13
| RP | Watts | LF009M3PCQT | 0.75 | H | 2015-03-13
| RP | Watts | LF009PCQT | 0.5 | H | 2015-03-13
| RP | Watts | LF909M1PCQT | 1.25 | H | 2015-03-13
| RP | Watts | LF909M1PCQT | 1.5 | H | 2015-03-13
| RP | Watts | LF909M1PCQT | 2 | H | 2015-03-13
| RP | Watts | LF909PCQT | 0.75 | H | 2015-03-13
| RP | Watts | LF909PCQT | 0.75 | VU | 2015-03-13
| RP | Watts | LF909PCQT | 1 | H | 2015-03-13
| RP | Watts | LF909PCQT | 1 | VU | 2015-03-13
| RP | Apollo/Conbraco | RPLF4AN | 2.5 | VUVD | 2015-02-27
| RP | Apollo/Conbraco | RPLF4AN | 2.5 | VUVU | 2015-02-27
| RP | Apollo/Conbraco | RPLF4AN | 3 | VUVD | 2015-02-27
| RP | Apollo/Conbraco | RPLF4AN | 3 | VUVU | 2015-02-27
Double Check Detector Assemblies-Type II
| DCDA-II | Febco | LF856 | 4 | H | 2015-01-26
| DCDA-II | Febco | LF856 | 4 | VU | 2015-01-26
| DCDA-II | Febco | LF876V | 4 | VUVD | 2015-01-26
| DCDA-II | Febco | LF876V | 4 | VUVU | 2015-01-26
Double Check Detector Assemblies-Type II
| DCDA-II | Febco | LF876V | 6 | VUVD | 2015-01-26
| DCDA-II | Febco | LF876V | 6 | VUVU | 2015-01-26
| DCDA-II | Febco | LF856 | 6 | H | 2015-03-13
| DCDA-II | Febco | LF856 | 6 | VU | 2015-03-13
| DCDA-II | Febco | LF856 | 2.5 | H | 2015-03-20
| DCDA-II | Febco | LF856 | 2.5 | VU | 2015-03-20
| DCDA-II | Febco | LF876V | 2.5 | VUVD | 2015-03-20
| DCDA-II | Febco | LF876V | 2.5 | VUVU | 2015-03-20
| DCDA-II | Febco | LF856 | 3 | H | 2015-03-20
| DCDA-II | Febco | LF856 | 3 | VU | 2015-03-20
| DCDA-II | Febco | LF876V | 3 | VUVD | 2015-03-20
| DCDA-II | Febco | LF876V | 3 | VUVU | 2015-03-20
Reduced Pressure Principle Detector Assemblies-Type II
| RPDA-II | Febco | LF866 | 4 | H | 2015-01-26
| RPDA-II | Febco | LF886V | 4 | VUVD | 2015-01-26
| RPDA-II | Febco | LF886V | 4 | VUVU | 2015-01-26
| RPDA-II | Febco | LF886V | 6 | VUVD | 2015-01-26
| RPDA-II | Febco | LF886V | 6 | VUVU | 2015-01-26
| RPDA-II | Febco | LF866 | 6 | H | 2015-03-13
| RPDA-II | Febco | LF866 | 2.5 | H | 2015-03-20
| RPDA-II | Febco | LF866 | 2.5 | VU | 2015-03-20
| RPDA-II | Febco | LF866 | 3 | H | 2015-03-20
| RPDA-II | Febco | LF866 | 3 | VU | 2015-03-20
| RPDA-II | Febco | LF886V | 2.5 | VUVD | 2015-03-20
| RPDA-II | Febco | LF886V | 2.5 | VUVU | 2015-03-20
| RPDA-II | Febco | LF886V | 3 | VUVD | 2015-03-20
| RPDA-II | Febco | LF886V | 3 | VUVU | 2015-03-20
| RPDA | Apollo/Conbraco | RPDALF4AN | 6 | VUVD | 2015-05-12
| RPDA | Apollo/Conbraco | RPDALF4AN | 6 | VUVU | 2015-05-12
Spill Resistant Pressure Vacuum Breakers
| SVB | Watts | LF008PCQT | 0.375 | VUH | 2015-03-13
| SVB | Watts | LF008PCQT | 0.5 | VUH | 2015-03-13
| SVB | Watts | LF008PCQT | 0.75 | VUH | 2015-03-13
| SVB | Watts | LF008PCQT | 1 | VUH | 2015-03-13

## Shutoff Valves
Shutoff Valve Designations
|  | (ttt) | Clow R/W Model 2639 (GxG) - OSY (2 1/2" - 3")
Clow R/W Model 2638 (GxFG) - OSY (4" - 10")
(formerly Clow Series F6137-OSY)
|  | (uuu) | Apollo Series 7H-QT
|  | (vvv) | Clow R/W Model 2640 (FxF) - OSY Post Indicator/Tapping Valve
(formerly Clow R/W F6136-OSY Post Indicator/Tapping Valve)
|  | (www) | Clow R/W Model 2639 (GxF) - OSY (2 1/2" - 3") Post Indicator/Tapping Valve
Clow R/W Model 2640 (GxF) - OSY (4" - 10") Post Indicator/Tapping Valve
(formerly Clow R/W F6138-OSY Post Indicator/Tapping Valve)
|  | (xxx) | Ningbo Union Ball Valves (Febco 622UF & 622UFT & Wilkins 850U-QT)(1/2" - 2" Ball Valve QT)
(aa) | American Figure 1-QT | (yyy) | Victaulic Series 702 (Butterfly valves)
(bb) | American Figure 17-NRS RW | (zzz) | Kennedy Model KS-RW Figure 7092ABF (FxG) - OSY
(cc) | American Figure 370OSY RW |  | (formerly Kennedy Series 7092ABF-OSY)
(dd) | Apollo Series 7B-QT | (aaaa) | Union Model GV12 (flange by groove)-OSY
(ee) | AVK Series 25-NRS | (bbbb) | Enbee Model GV12 (flange by groove)-OSY
(ff) | AVK Series 25-OSY (Nibco F607RW OSY) | (cccc) | Kennedy Model KS-RW Figure 7092 (FxG) - OSY
(gg) | Clow R/W Model 2640 (FxF) - NRS |  | (formerly Kennedy Series 7092 (GxF) - OSY)
| (formerly Clow R/W F6102-NRS) | (dddd) | Kennedy Model KS-RW Figure 7592 (FxG) - NRS
(hh) | Clow R/W Model 2640 (FxF) - OSY |  | (formerly Kennedy Series 7592ABF - NRS)
| (formerly Clow R/W F6136-OSY) | (eeee) | Kennedy Model KS-RW Figure 7592PABF (FxG) - NRS Post Indicator/Tapping Valve
(ii) | Fortune Series 620/623 (C84400 Bronze) (Formerly Figure 601) |  | (formerly Kennedy Series 7592PABF-Post Indicator/Tapping Valve)
| Private labeled as: Ames, Buckner, Febco, Flomatic, Hersey and Wilkins | (ffff) | Watts Model 409 (2-1/2" - 10" OSY-RW FxF)
(jj) | Kennedy Ken Seal I-NRS | (gggg) | Watts Model 409 (2-1/2" - 10" OSY-RW FxG)
(kk) | Kennedy Ken Seal-OSY | (hhhh) | Watts Model LF-FBV & LF-FBV-E (1/4" - 2" Ball Valve QT)
(ll) | Kennedy Model KS-FW Figure 8561 (FxF) - NRS (2 1/2" - 10") |  | Ames Model LF-FBV & LF-FBV-E (1/4" - 2" Ball Valve QT)
| Kennedy Model KS-RW Figure 7561 (FxF) - NRS (4" - 10") |  | Febco Model LF-FBV & LF-FBV-E (1/4" - 2" Ball Valve QT)
| (formerly Kennedy Ken Seal II-NRS) | (iiii) | Wilkins Series 850XL (850TXL) - QT
(mm) | Kennedy Model KS-FW Figure 8068 (FxF) - OSY (2 1/2" - 10") | (jjjj) | WATTS Model 409 (2" OSY-RW NPTxNPT)
| Kennedy Model KS-RW Figure 7068 (FxF) - OSY (4" - 10") | (kkkk) | Kennedy Model KS-RW Figure 7093 (GxG) - OSY
| (formerly Kennedy Ken Seal II-OSY) | (llll) | Kennedy Model KS-RW Figure 7593 (GxG) - NRS
(nn) | Lee Brass-QT | (mmmm) | Kennedy Model KS-RW Figure 7093ABF (GxG) - OSY
(oo) | Watts Model 405 (2-1/2" - 10" NRS-RW FxF) | (nnnn) | Kennedy Model KS-RW Figure 7593ABF (GxG) - NRS
(pp) | Watts Model 408 (2-1/2" - 10" OSY-RW FxF) | (oooo) | Kennedy Model KS-RW Figure 7593PABF (GxG) - NRS Post Indicator
(qq) | Mueller R/W HP NRS | (pppp) | Watts Model L-FBV & L-FBV-E (1/4" - 2" Ball Valve QT)
(rr) | Mueller R/W HP OSY |  | Ames Model L-FBV & L-FBV-E (1/4" - 2" Ball Valve QT)
(ss) | Toro.Orion Integral Ball Valve-QT |  | Febco Model L-FBV & L-FBV-E (1/4" - 2" Ball Valve QT)
(tt) | American Flow Control (Waterous) Series 500-NRS | (qqqq) | Kennedy Figure G300E - Butterfly Valve (4",6")
(uu) | American Flow Control (Waterous Series 500-OSY | (rrrr) | Kennedy Figure 02G - Butterfly Valve (8")
(vv) | Watts Model FBV & FBV-E (1/4" - 2" Ball Valve QT) | (ssss) | Wilkins Model 48 (GXF) - NRS (2-1/2" - 12")
| Ames Model FBV & FBV-E (1/4" - 2" Ball Valve QT) | (tttt) | Wilkins Model 48 (FXF) - NRS (2-1/2" - 12")
(ww) | Watts Moel G4000-FDA (2-1/2" -10" Ball Valve FxF) | (uuuu) | Wilkins Model 48 (GXG) - NRS (2-1/2" - 12") Post Indicator/Tapping Valve
(xx) | Watts Model 6080 & 6080-E (1/4" - 2" Ball Valve QT) | (vvvv) | Wilkins Model 48 (GXF) - NRS (2-1/2" - 12") Post Indicator/Tapping Valve
(yy) | Matco-Norca 10RW (NRS) | (wwww) | Wilkins Model 48 (FXF) - NRS (2-1/2" - 12") Post Indicator/Tapping Valve
(zz) | Matco-Norca 105U (OSY) | (xxxx) | Wilkins Model 48 (GXG) - OSY (2-1/2" - 12")
(aaa) | American Flow Control Series 2500-NRS | (yyyy) | Wilkins Model 48 (GXF) - OSY (2-1/2" - 12")
(bbb) | American Flow Control Series 2500-OSY
(ccc) | M&H Model 4067-02 (NRS) | (zzzz) | Wilkins Model 48 (FXF) - OSY (2-1/2" - 12")
(ddd) | M&H Model 4068-02(OSY) | (aaaaa) | Wilkins Model 48 (GXG) - NRS (2-1/2" - 12")
(eee) | Stockham Model G-610 (OSY) | (bbbbb) | Milwaukee BB-SC100 - Butterfly Valve
(fff) | Febco Series 620 QT | (ccccc) | Milwaukee BB-SCS02 - Butterfly Valve (with gearbox)
(ggg) | Fortune Figure 620U-QT | (ddddd) | Flomatic Model NRS
(hhh) | Watts Model S-FBV & S-FBV-E (1/4" - 1" Ball Valve QT) | (eeeee) | Watts Model FBV-FP & FBV-E-FP (3/4" - 2" Ball Valve w/Gearbox)
(iii) | Mueller Model A2360-NRS |  | Ames Model LFAFBV-FP & LFAFBV-E-FP (3/4" - 2" Ball Valve w/Gearbox)
(int) | Shutoff Valve is integral part of assembly | (fffff) | Watts Model L-FBV-QT (2-1/2" - 4" Ball Valve NPTxG)
(jjj) | Febco Series 621-QT | (ggggg) | Wilkins Model 850MSS
(kkk) | Febco Series 620U-QT | (hhhhh) | Fortune Series 620/623 (c89520 unleaded bronze)
(lll) | Mueller Model R2360-OSY | (iiiii) | Apollo Series 77B-100 and 77C-100 - QT
(mmm) | Conbraco Series IBVE-125-QT | (jjjjj) | Apollo Series 77BLF-100 and 77CLF-100 - QT
(nnn) | Kennedy Model KS-FW Figure 8701 (FxF) - NRS (3" - 10") Post Indicator/Tapping | (kkkkk) | Wilkins Model 49 (GXF) - (2 1/2" - 10")
| Kennedy Model KS-RW Figure 7701 (FxF) - NRS (4" - 10") Post Indicator/Tapping | (lllll) | Wilkins Model 49 (GXG) - (2 1/2" - 10")
| (formerly Kennedy Ken Seal II Post Indicator/Tapping) | (mmmmm) | Wilkins 850UXL (850TUXL) -QT
(ooo) | Ningbo Ball Valves (Febco 622F & 622FT, Watts Series 855-QT & Wilkins Series 850-QT)(1/4" - 2" Ball Valve QT) | (nnnnn) | Watts Model 405 (2 1/2" - 10" NRS-RW FxG)
(ppp) | Clow R/W Model 2639 (GxF) - NRS (2 1/2" - 3") | (ooooo) | ARI HC260 and HC262 Ball Valves - QT
| Clow R/W Model 2638 (GxF) - NRS (4" - 10") | (ppppp) | Febco Model LF622UF & LF622UFT (1/2" - 2" Ball Valve QT)
| (formerly Clow Series F6105-NRS) | (qqqqq) | Febco Model LF622F & LF622FT (1/2" - 2" Ball Valve QT)
(qqq) | Clow R/W Model 2639 (GxF) - OSY (2 1/2" - 3") | (rrrrr) | Watts Model LFFBV-FRG & LFFBV-E-FRG (1/2" - 2" Ball Valve QT)
| Clow R/W Model 2638 (GxF) - OSY (4" - 10") | (sssss) | Apollo Series 91B and 91C-QT (1/2 - 2")
| (formerly Clow Series F6138-OSY) | (ttttt) | Apollo Series 91BLF and 91CLF-QT (1/2 - 2")
(rrr) | Apollo Series 7B-308-01 (& 7B-308-31) | (uuuuu) | Apollo Model 77B-LFU and 77C-LFU Union Ball Valves - QT (1/2")
(sss) | Clow R/W Model 2639 (GxG) - NRS (2 1/2" - 3") | (vvvvv) | Apollo Series 91BLF-U and 91CLF-U-QT (3/4"-2")
| Clow R/W Model 2638 (GxFG) - NRS (4" - 10") | (wwwww) | Apollo Series 91B-U and 91C-U-QT (3/4"-2")
(formerly Clow Series F6104-NRS)

## Meters
Detector Assembly Meters
A | Hersey Model F-F 5/8" x 3/4"
B | Carlon 5/8" x 3/4"
C | Dandé Model D-3 5/8" x 3/4"
D | Gamon-Calmet 5/8"
E | Hays Acumeter 5/8" x 3/4"
F | Arad 5/8" x 3/4" (Master Meter)
G | Schlumberger 5/8" x 3/4" Model MBRF
H | Rockwell (Sensus) SR-II 5/8" x 3/4"
I | Hersey Model 430 - 5/8"
J | Elster AMCO Model C700 5/8”x3/4” (Formerly Kent, ABB)
K | Precision 5/8"
L | Neptune Trident 8 5/8"
M | Neptune T-10 5/8"(Lead free compliant version identified with NSF61 mark on meter)
N | Badger Model 25 3/4"
O | Badger 5/8" x 3/4" Model 25 (Lead free compliant version identified with NSF61 mark on meter)
P | Hersey Model 430 Series II 5/8"
Q | Hersey Model MVR-30 3/4"
R | Neptune T-10 1"
S | Neptune T-10 1 1/2"

## Manufacturers
Manufacturers of Approved Backflow Prevention Assemblies
Ames Fire & Waterworks - A Watts Water Technologies Company | Flomatic
http://www.amesfirewater.com/ | http://www.flomatic.com/
1427 N. Market Blvd., Ste. 9 | 15 Pruyn’s Island Dr.
Sacramento, CA 95834 | Glen Falls, NY 12801-4424
(916) 928-0123 | (800) 833-2040
Apollo/Conbraco Industries, Inc. | Hersey Meters
http://www.apollovalves.com/ | http://www.herseymeters.com/
P. O. Box 247 | 10210 Statesville Blvd.
Matthews, NC 28105 | Cleveland, NC 27013
(704) 847-9191 | (800) 323-8584
A.R.I. FLOW CONTROL ACCESSORIES | Watts - A Watts Water Technologies Company
http://www.arivalves.com | http://www.wattsreg.com/
Kibbutz Kfar Charuv | 815 Chestnut Street
M.P. South Golan | North Andover, MA 01845
ISRAEL, 12932 | (978) 688-1811
972-4-6761800 or 972-4-6761988
Wilkins Regulator Company
Arrowhead Brass | http://www.zurn.com/operations/wilkins/pages/home.asp
http://www.arrowheadbrass.com/ | 1747 Commerce Way
5147 Alhambra Ave. | Paso Robles, CA 93446
Los Angeles, CA 90032 | (800) 817-8177
(323) 343-9790
Cash Acme
http://www.cashacme.com
2400 7th Avenue S.W.
Cullman, Alabama 35055
(256) 775-8200
Cla-Val Company
http://www.cla-val.com/
P. O. Box 1325
Newport Beach, CA 92659-0325
(949) 722-4800
FEBCO - A Watts Water Technologies Company
http://www.febcoonline.com
P. O. Box 8070
Fresno, CA 93747
(559) 252-0791

## Special Notices
Special Notices
From time to time the Foundation issues Special Notices when specific information needs to be brought before the Members of the Foundation. A copy of the notices are sent to Foundation Members as they are published. Notices may also be found on the Internet at the World Wide Web address of http://www.usc.edu/fccchr/notice.html
Notices are summarized as follows.
Notice 96-001
This notice lists Ames assemblies which have been reported with low check valve readings. Corrections to the problem are discussed.
Notice 97-001
This Notice discusses changes in the Wilkins 975 8” and 10” reduced pressure principle assemblies. A change in the retaining cup in the relief valve stem.
Notice 97-002
This notice identifies Ames 2000SS, 3000SS, and 4000SS series assemblies were discovered to have unapproved components.
Notice 97-003
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 98-001
This notice advises members of certain action in the Federal Register regarding cross-connection control programs.
Notice 98-002
This notice advises members of Wilkins 950 series and 975 series modifications.
Notice 99-001
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 99-002
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 99-003
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 01-001
Discuss silicon parts in certain Febco relief valves
Notice 01-002/Revised Notice 01-002-R1
This notice discusses some check valves not approved in certain Ames and Watts asemblies
Notice 01-003
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 02-001
This notice explains there are some specific Febco assemblies with unapproved check valve retainers.
Notice 03-001
This notice explains there are some improper markings of model designations on some Wilkins assemblies
Notice 03-002
This notice explains there is the possibility of the interference of the check valves on some Ames and Watts assemblies
Notice 04-001
This notice identifies some Febco 825YA assemblies sold with a dimensional variation
Notice 05-001
This Notice identifies some Ames and Watts assemblies sold with unapproved disc material.
Notice 06-001
This notice identifies unapproved guides found in certain Febco assemblies
Notice 06-002
This notice identifies a change in the design of the Flomatic PVBs
Notice 06-003
Notice regarding Cash-Acme Assemblies
Notice 07-001
Out of tolerance springs on Conbraco assemblies
Notice 09-001
Unapproved Third party components are being distributed
Notice 13-001
Modifications to guiding surfaces of the check valves on Wilkins Assemblies
Notice 14-001
Clarifies the Approval status of Apollo/Conbraco backflow prevention assemblies
The following should be considered before selecting a particular assembly:
1. All local plumbing laws and regulations must be adhered to.
2. All backflow prevention assemblies shall be installed in accordance with specifications furnished by the Public Works Commission and the Manufacturer's installation instructions (PWC's installation instructions supersedes the Manufacture's instructions, due to local requirements).
3. Reduced pressure principle assemblies must be installed in a horizontal position and in a location in which no portion of the assembly can become submerged under any circumstances (pit/below grade installations are prohibited).
4. The operation and performance of these assemblies may vary among manufacturers because of design and local pressure conditions.
5. The Public Works Commission of the City of Fayetteville reserves the right to add to or remove from the approved list any Reduced Pressure Backflow Prevention Assembly, Double Check Valve Assembly, or Pressure Vacuum Breaker Backflow Preventer.
6. It is a requirement that backflow prevention assemblies be tested immediately after installation and at least once a year thereafter by a person approved by the Public Works Commission. A copy of the test results must be sent to the Public Works Commission System Protection Office immediately after testing (within 10 days). Any time that repairs to backflow prevention assemblies are deemed necessary, whether through initial or annual testing or routine inspection by the owner or by the Public Works Commission, these repairs must be completed within a specified time in accordance with the degree of hazard. In no case shall this time period exceed thirty (30) days. Should you have any questions concerning the above mentioned testing requirements, contact Brian Morrison, Public Works Commission, at (910) 223-4704.
7. By-pass piping is not permitted unless the by-pass piping is equipped with an approved backflow prevention assembly of the same type and brand as the main line assembly. In many instances it will be necessary to install two approved backflow prevention assemblies in order that water service will not be interrupted during the testing/repair of the assembly.
8. Personnel of the Public Works Commission will conduct testing of backflow prevention assemblies on a random basis to ensure that the assemblies are operating properly. The owner will be giving adequate advance notification prior to the test.
9. When cross-connections are found to exist, the owner, his agent, occupant, or tenant will be notified in writing to disconnect the same within the time limit established by the Public Works Commission. Degree of protection required and maximum time allowed for compliance will be based upon the potential degree of hazard to the public water system. The maximum time limits are as follows:
a. Cross-connections shall be corrected through one of the following: elimination, air gap separation, reduced pressure zone backflow prevention assembly, double check valve assembly, or pressure vacuum breaker.
b. Cross-connections with private wells or other unapproved auxiliary of water is prohibited and requires immediate disconnection.
c. Corrections, cross connection eliminations, or backflow prevention assembly installations on health hazard facilities shall be made within sixty (60) days upon notification.
d. Corrections, cross connection eliminations, or backflow prevention assembly installations on non-health hazard facilities shall be made within ninety (90) days upon notification.
NOTE:
All assemblies approved for use in the PWC system must have prior approval by Foundation for Cross-Connection Control and Hydraulic Research, University of Southern California. All assemblies are approved for potable water services only.
Backflow Prevention Assemblies two (2) inches and smaller shall have one quarter (1/4) turn, full port, resilient seated, bronze ball valve shut-off. Assemblies two and one half (2 1/2) inches and larger shall have resilient wedge shut-off valves; the backflow preventer and resilient wedge shut-off valves must be fuse bonded epoxy coated.
All backflow prevention assemblies used for domestic use must be a led free product.